## Cover
Prepared for:
Design Trust for Public Spaces
DESIGN GUIDELINES
ROUGH ORDER OF MAGNITUDE STATEMENT OF PROBABLE COST
ISSUE | Rev 0 | 2015-11-06
Arup North America Ltd.
560 Mission Street, Suite 700
San Francisco, CA 94105
United States of America
t : + 1 415.957.9445
f : + 1 415.957.9096
www.arup.com

## Basis of Estimate
2015-11-06
DESIGN GUIDELINES
MECHANICAL - ELECTRICAL - PLUMBING SYSTEMS FOR RETAIL SPACES
ROUGH ORDER OF MAGNITUDE STATEMENT OF PROBABLE COST
PROJECT NOTES & BASIS OF ESTIMATE
1 | Project Description
The Design Trust for Public Spaces, in partnership with NYC Department of Housing Preservation and Development is preparing the design guidelines for Retail and other floor uses in affordable housing developments.
2 | Basis of Estimate
This estimate is classified as a Level 5 within the Arup Cost Estimate Classification Tool and was generated by means of widely used and accepted estimating practices.
Pricing shown reflects probable construction costs obtainable in the New York area on the date of this document. This estimate is a determination of fair market value for the construction of this project. It is not a prediction of low bid. Pricing assumes competitive bidding for every portion of the construction work for all subcontractors, that is to mean 4 to 5 bids. If fewer bids are received, bid results can be expected to be higher.
This document is based on the measurement and pricing of quantities taken from a high level design option. Therefore, the quantities are subject to change as the design progresses.
Subcontractor’s markups have been included in each line item unit price. These markups cover the cost of field overhead, home office overhead, and profit. These markups can range from 5% to 15% of the cost for that particular item of work. The rates that have been established are for budgetary purposes only and are not to be used to establish the cost of additions or deletions to the scope of work that may arise during the actual construction process.
This estimate assumes the engineering features would be installed as part of a "New" or "Initial Build" construction project and excludes any initial contractor mobilization costs that would be needed if these features were to be procured individually.
The estimate within this document is not intended to set the budget for the potential work. The budget can only be established once the design solutions have been thoroughly developed and the Forecasted Costs subsequently approved by the Owner.
Costs will be updated as the design develops in later stages and the level of estimate detail will be progressed in relation to the design
This cost estimate reflects only the line items provided and does not include any cost for items that may be impacted as a result of these engineering features
Estimate includes no third party costs, owner's costs, or escalation
4 | Documentations
Design Guidelines for Retail and Other Ground Floor Uses In Affordable Housing Developments, Design Trust
5 | Project Construction Schedule
TBD
6 | Indirect Costs, Overhead and Profit
Indirect Costs, Overhead and Profit have not been included in this exercise.
7 | Soft Costs
Soft costs have not been included in this exercise
8 | Contingency
Design and Construction Contingency have not been included in this exercise.
9 | Escalation
The costs presented herein are based on Qtr 2 2015 USD. No escalation has been included.
10 | Assumptions
Easy access to the work area with minimal constraints.
Normal bidding climate.
Staging area within reasonable distance from the site.
All work done during normal business hours.
11 | Items excluded from the Cost Estimate
Land acquisition fees
Legal and accounting fees
Financing charges
Fire and all risk insurance
Hazardous material mitigation
The costs or impacts of latent environmental issues that result in litigations or development delays
Planning and enquiry costs including legal expenses and fees
Bid contingency
Cost escalation beyond the date of this estimate
Permits
QAQC
Local statutory regulations
12 | Items that may affect the cost estimate
Modifications to the scope of work included in this estimate.
Special phasing requirements.
Restrictive technical specifications or excessive contract conditions.
Any other non-competitive bid situations.
Bids delayed beyond the projected schedule.
13 | Statements of Probable Cost
ARUP has no control over the cost of labor and materials, general contractor’s or any subcontractor’s method of determining prices, or competitive bidding and market conditions. This opinion of probable cost of construction is made on the basis of the experience, qualifications, and best judgment of the professional consultant familiar with the construction industry. ARUP cannot and does not guarantee that proposals, bids, or actual construction costs will not vary from this or subsequent cost estimates.
15 | Recommendation for Cost Control
ARUP recommends that the Owner carefully review this document, including line item descriptions, unit prices, clarifications, exclusions, inclusions and assumptions, contingencies, escalation and markups. If the project is over budget, or if there are unresolved budgeting issues, alternate systems schemes should be evaluated before proceeding into the construction phase.
16 | Request for Modifications
Requests for modifications of any apparent errors or omissions to this document must be made to ARUP within thirty (30) days of receipt of this estimate. Otherwise, it will be understood that the contents have been concurred with and accepted.

## Estimate Classification
Estimate Classification Matrix

## Summary
Cost Summary
| Retail Use | Area | Cost Range |  |  | $/SF Likely
|  |  | Low -20% | Likely | High +50%
| Supermarket | 12000 | 712744 | 890930 | 1336395 | 74.2442
| Pharmacy (L) | 12000 | 683136 | 853920 | 1280880 | 71.16
| Pharmacy (S) | 6000 | 434424 | 543030 | 814545 | 90.505
| Health Care Center | 4000 | 372936 | 466170 | 699255 | 116.5425
| Full Service Restaurant | 4000 | 527424 | 659280 | 988920 | 164.82
| General Retail (L) | 4000 | 335664 | 419580 | 629370 | 104.895
| General Retail (S) | 2000 | 233336 | 291670 | 437505 | 145.835
| Laundromat | 2000 | 318752 | 398440 | 597660 | 199.22

## Cost Matrix Tool
COST MATRIX TOOL
This is a tool for the designer or user that will faciltate the decision process regarding design options and cost allocation.
Each system has a design option (a,b,c,d) and a cost allocation possibility (developer, tenant, shared).
Those options appear on a drop-down menu. Select the design option (a, b, c, d) and the cost allocation for the Developer (Developer, Developer + Either Party), The cost allocation for the Tenant updates automatically.
Once the option and the cost allocation have been selected, the costs update automatically.
[8 empty] | 24000 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
Supermarket |  |  | Space area: |  |  | $ / SF | Pharmacy (L) |  |  | Space area: |  |  | $ / SF | Pharmacy (S) |  |  | Space area: |  |  | $ / SF | Health Care Center |  |  | Space area: |  |  | $ / SF | Full Service Restaurant |  |  | Space area: |  |  | $ / SF | General Retail (L) |  |  | Space area: |  |  | $ / SF | General Retail (S) |  |  | Space area: |  |  | $ / SF | Laundromat |  |  | Space area: |  |  | $ / SF
|  |  | 12000 | [6 empty] | 12000 | [6 empty] | 6000 | [6 empty] | 4000 | [6 empty] | 4000 | [6 empty] | 4000 | [6 empty] | 2000 | [6 empty] | 2000
1 | Mechanical | [5 empty] | 1 | Mechanical | [5 empty] | 1 | Mechanical | [5 empty] | 1 | Mechanical | [5 empty] | 1 | Mechanical | [5 empty] | 1 | Mechanical | [5 empty] | 1 | Mechanical | [5 empty] | 1 | Mechanical
1.1 | Heating |  | Developer Cost |  | Tenant Cost |  | 1.1 | Heating |  | Developer Cost |  | Tenant Cost |  | 1.1 | Heating |  | Developer Cost |  | Tenant Cost |  | 1.1 | Heating |  | Developer Cost |  | Tenant Cost |  | 1.1 | Heating |  | Developer Cost |  | Tenant Cost |  | 1.1 | Heating |  | Developer Cost |  | Tenant Cost |  | 1.1 | Heating |  | Developer Cost |  | Tenant Cost |  | 1.1 | Heating |  | Developer Cost |  | Tenant Cost
a |  | Developer | 166500 | Tenant + Either party | 48000 | 17.875 | d |  | Developer | 12500 | Tenant + Either party | 96000 | 9.0417 | d |  | Developer | 12500 | Tenant + Either party | 48000 | 10.0833 | d |  | Developer + Either party | 44500 | Tenant | 0 | 11.125 | a |  | Developer | 92500 | Tenant + Either party | 16000 | 27.125 | a |  | Developer | 47500 | Tenant + Either party | 16000 | 15.875 | a |  | Developer | 29500 | Tenant + Either party | 8000 | 18.75 | a |  | Developer | 58500 | Tenant + Either party | 8000 | 33.25
1.2 | Cooling | [5 empty] | 1.2 | Cooling | [5 empty] | 1.2 | Cooling | [5 empty] | 1.2 | Cooling | [5 empty] | 1.2 | Cooling | [5 empty] | 1.2 | Cooling | [5 empty] | 1.2 | Cooling | [5 empty] | 1.2 | Cooling
c |  | Developer + Either party | 67500 | Tenant | 0 | 5.625 | a |  | Developer | 106500 | Tenant + Either party | 0 | 8.875 | a |  | Developer | 100500 | Tenant + Either party | 0 | 16.75 | a |  | Developer + Either party | 94500 | Tenant | 0 | 23.625 | a |  | Developer | 94500 | Tenant + Either party | 0 | 23.625 | a |  | Developer + Either party | 94500 | Tenant | 0 | 23.625 | a |  | Developer + Either party | 85500 | Tenant | 0 | 42.75 | a |  | Developer + Either party | 85500 | Tenant | 0 | 42.75
1.3 | Ventilation | [5 empty] | 1.3 | Ventilation | [5 empty] | 1.3 | Ventilation | [5 empty] | 1.3 | Ventilation | [5 empty] | 1.3 | Ventilation | [5 empty] | 1.3 | Ventilation | [5 empty] | 1.3 | Ventilation | [5 empty] | 1.3 | Ventilation
a |  | Developer | 6000 | Tenant + Either party | 60000 | 5.5 | a |  | Developer + Either party | 69000 | Tenant | 0 | 5.75 | a |  | Developer | 4000 | Tenant + Either party | 60000 | 10.6667 | a |  | Developer | 1500 | Tenant + Either party | 60000 | 15.375 | a |  | Developer | 63000 | Tenant + Either party | 0 | 15.75 | a |  | Developer | 2000 | Tenant + Either party | 60000 | 15.5 | a |  | Developer | 1000 | Tenant + Either party | 60000 | 30.5 | a |  | Developer | 2000 | Tenant + Either party | 60000 | 31
1.4 | Air-Side Economizers | [5 empty] | 1.4 | Air-Side Economizers | [5 empty] | 1.4 | Air-Side Economizers | [5 empty] | 1.4 | Air-Side Economizers | [5 empty] | 1.4 | Air-Side Economizers | [5 empty] | 1.4 | Air-Side Economizers | [5 empty] | 1.4 | Air-Side Economizers | [5 empty] | 1.4 | Air-Side Economizers
a |  | Developer + Either party | 0 | Tenant | 0 | 0 | a |  | Developer + Either party | 0 | Tenant | 0 | 0 | a |  | Developer | 0 | Tenant + Either party | 0 | 0 | a |  | Developer | 0 | Tenant + Either party | 0 | 0 | a |  | Developer + Either party | 0 | Tenant | 0 | 0 | a |  | Developer | 0 | Tenant + Either party | 0 | 0 | a |  | Developer | 0 | Tenant + Either party | 0 | 0 | a |  | Developer | 0 | Tenant + Either party | 0 | 0
1.5 | Exhaust Air | [5 empty] | 1.5 | Exhaust Air | [5 empty] | 1.5 | Exhaust Air | [5 empty] | 1.5 | Exhaust Air | [5 empty] | 1.5 | Exhaust Air | [5 empty] | 1.5 | Exhaust Air | [5 empty] | 1.5 | Exhaust Air | [5 empty] | 1.5 | Exhaust Air
a |  | Developer | 6000 | Tenant + Either party | 11000 | 1.4167 | a |  | Developer + Either party | 17000 | Tenant | 0 | 1.4167 | a |  | Developer + Either party | 17000 | Tenant | 0 | 2.8333 | a |  | Developer | 6000 | Tenant + Either party | 11000 | 4.25 | a |  | Developer | 12000 | Tenant + Either party | 22000 | 8.5 | a |  | Developer | 6000 | Tenant + Either party | 11000 | 4.25 | a |  | Developer | 6000 | Tenant + Either party | 11000 | 8.5 | a |  | Developer | 0 | Tenant + Either party | 0 | 0
1.6 | Kitchen Exhaust | [5 empty] | 1.6 | Kitchen Exhaust | [5 empty] | 1.6 | Kitchen Exhaust | [5 empty] | 1.6 | Kitchen Exhaust | [5 empty] | 1.6 | Kitchen Exhaust | [5 empty] | 1.6 | Kitchen Exhaust | [5 empty] | 1.6 | Kitchen Exhaust | [5 empty] | 1.6 | Kitchen Exhaust
a |  | Developer | 1500 | Tenant + Either party | 25000 | 2.2083 | a |  | Developer + Either party | N/A | Tenant | N/A | 0 | a |  | Developer | N/A | Tenant + Either party | N/A | 0 | a |  | Developer | N/A | Tenant + Either party | N/A | 0 | a |  | Developer | 1600 | Tenant + Either party | 25000 | 6.65 | a |  | Developer | N/A | Tenant + Either party | N/A | 0 | a |  | Developer | N/A | Tenant + Either party | N/A | 0 | a |  | Developer | N/A | Tenant + Either party | N/A | 0
1.7 | Air-Handling Units | [5 empty] | 1.7 | Air-Handling Units | [5 empty] | 1.7 | Air-Handling Units | [5 empty] | 1.7 | Air-Handling Units | [5 empty] | 1.7 | Air-Handling Units | [5 empty] | 1.7 | Air-Handling Units | [5 empty] | 1.7 | Air-Handling Units | [5 empty] | 1.7 | Air-Handling Units
d |  | Developer | 0 | Tenant + Either party | 57500 | 4.7917 | a |  | Developer | 0 | Tenant + Either party | 90190 | 7.5158 | a |  | Developer + Either party | 0 | Tenant | 46250 | 7.7083 | a |  | Developer | 0 | Tenant + Either party | 27500 | 6.875 | a |  | Developer | 0 | Tenant + Either party | 35000 | 8.75 | a |  | Developer | 0 | Tenant + Either party | 27500 | 6.875 | a |  | Developer | 0 | Tenant + Either party | 19000 | 9.5 | a |  | Developer | 0 | Tenant + Either party | 19000 | 9.5
1.8 | Intakes and Exhaust | [5 empty] | 1.8 | Intakes and Exhaust | [5 empty] | 1.8 | Intakes and Exhaust | [5 empty] | 1.8 | Intakes and Exhaust | [5 empty] | 1.8 | Intakes and Exhaust | [5 empty] | 1.8 | Intakes and Exhaust | [5 empty] | 1.8 | Intakes and Exhaust | [5 empty] | 1.8 | Intakes and Exhaust
a |  | Developer + Either party | 6000 | Tenant | 0 | 0.5 | b |  | Developer + Either party | 65000 | Tenant | 0 | 5.4167 | a |  | Developer | 4000 | Tenant + Either party | 0 | 0.66667 | b |  | Developer | 65000 | Tenant + Either party | 0 | 16.25 | b |  | Developer | 65000 | Tenant + Either party | 0 | 16.25 | a |  | Developer | 2000 | Tenant + Either party | 0 | 0.5 | a |  | Developer | 1000 | Tenant + Either party | 0 | 0.5 | a |  | Developer | 2000 | Tenant + Either party | 0 | 1
2 | Electrical | [5 empty] | 2 | Electrical | [5 empty] | 2 | Electrical | [5 empty] | 2 | Electrical | [5 empty] | 2 | Electrical | [5 empty] | 2 | Electrical | [5 empty] | 2 | Electrical | [5 empty] | 2 | Electrical
2.1 | Separate metering for electricity by utility | [5 empty] | 2.1 | Separate metering for electricity by utility | [5 empty] | 2.1 | Separate metering for electricity by utility | [5 empty] | 2.1 | Separate metering for electricity by utility | [5 empty] | 2.1 | Separate metering for electricity by utility | [5 empty] | 2.1 | Separate metering for electricity by utility | [5 empty] | 2.1 | Separate metering for electricity by utility | [5 empty] | 2.1 | Separate metering for electricity by utility
a |  | Developer | 9550 | Tenant + Either party | 1000 | 0.87917 | a |  | Developer + Either party | 6850 | Tenant | 1000 | 0.57083 | a |  | Developer | 3300 | Tenant + Either party | 1000 | 0.71667 | a |  | Developer | 3300 | Tenant + Either party | 1000 | 1.075 | a |  | Developer | 6850 | Tenant + Either party | 1000 | 1.9625 | a |  | Developer | 3300 | Tenant + Either party | 1000 | 1.075 | a |  | Developer | 2750 | Tenant + Either party | 1000 | 1.875 | a |  | Developer | 3300 | Tenant + Either party | 1000 | 2.15
2.2 | Emergency Power | [5 empty] | 2.2 | Emergency Power | [5 empty] | 2.2 | Emergency Power | [5 empty] | 2.2 | Emergency Power | [5 empty] | 2.2 | Emergency Power | [5 empty] | 2.2 | Emergency Power | [5 empty] | 2.2 | Emergency Power | [5 empty] | 2.2 | Emergency Power
c |  | Developer | 28000 | Tenant + Either party | 1000 | 2.4167 | c |  | Developer + Either party | 23000 | Tenant | 1000 | 1.9167 | a |  | Developer + Either party | 0 | Tenant | 600 | 0.1 | a |  | Developer | 0 | Tenant + Either party | 450 | 0.1125 | a |  | Developer | 0 | Tenant + Either party | 450 | 0.1125 | a |  | Developer | 0 | Tenant + Either party | 600 | 0.15 | a |  | Developer | 0 | Tenant + Either party | 300 | 0.15 | a |  | Developer | 0 | Tenant + Either party | 300 | 0.15
2.3 | Fire Alarm | [5 empty] | 2.3 | Fire Alarm | [5 empty] | 2.3 | Fire Alarm | [5 empty] | 2.3 | Fire Alarm | [5 empty] | 2.3 | Fire Alarm | [5 empty] | 2.3 | Fire Alarm | [5 empty] | 2.3 | Fire Alarm | [5 empty] | 2.3 | Fire Alarm
a |  | Developer | 1000 | Tenant + Either party | 120000 | 10.0833 | a |  | Developer + Either party | 1000 | Tenant | 120000 | 0.083333 | a |  | Developer | 1000 | Tenant + Either party | 60000 | 10.1667 | a |  | Developer | 1000 | Tenant + Either party | 41240 | 10.56 | a |  | Developer | 1000 | Tenant + Either party | 40000 | 10.25 | a |  | Developer | 1000 | Tenant + Either party | 40000 | 10.25 | a |  | Developer | 1000 | Tenant + Either party | 20000 | 10.5 | a |  | Developer | 1000 | Tenant + Either party | 20000 | 10.5
3 | Plumbing | [5 empty] | 3 | Plumbing | [5 empty] | 3 | Plumbing | [5 empty] | 3 | Plumbing | [5 empty] | 3 | Plumbing | [5 empty] | 3 | Plumbing | [5 empty] | 3 | Plumbing | [5 empty] | 3 | Plumbing
3.1 | Domestic Water | [5 empty] | 3.1 | Domestic Water | [5 empty] | 3.1 | Domestic Water | [5 empty] | 3.1 | Domestic Water | [5 empty] | 3.1 | Domestic Water | [5 empty] | 3.1 | Domestic Water | [5 empty] | 3.1 | Domestic Water | [5 empty] | 3.1 | Domestic Water
a |  | Developer | 23500 | Tenant + Either party | 36000 | 4.9583 | a |  | Developer + Either party | 23500 | Tenant | 36000 | 1.9583 | a |  | Developer | 23500 | Tenant + Either party | 36000 | 9.9167 | a |  | Developer | 23500 | Tenant + Either party | 36000 | 14.875 | a |  | Developer | 23500 | Tenant + Either party | 36000 | 14.875 | a |  | Developer | 23500 | Tenant + Either party | 36000 | 14.875 | a |  | Developer | 9500 | Tenant + Either party | 12000 | 10.75 | a |  | Developer | 23500 | Tenant + Either party | 0 | 11.75
3.2 | Hot Water | [5 empty] | 3.2 | Hot Water | [5 empty] | 3.2 | Hot Water | [5 empty] | 3.2 | Hot Water | [5 empty] | 3.2 | Hot Water | [5 empty] | 3.2 | Hot Water | [5 empty] | 3.2 | Hot Water | [5 empty] | 3.2 | Hot Water
a |  | Developer | 21700 | Tenant + Either party | 36000 | 4.8083 | a |  | Developer + Either party | 21700 | Tenant | 36000 | 1.8083 | a |  | Developer + Either Party | 21700 | Tenant | 36000 | 9.6167 | c |  | Developer | 0 | Tenant + Either party | 2000 | 0.5 | a |  | Developer + Either Party | 21700 | Tenant | 36000 | 14.425 | a |  | Developer | 0 | Tenant + Either party | 0 | 0 | a |  | Developer | 0 | Tenant + Either party | 0 | 0 | a |  | Developer | 21700 | Tenant + Either party | 0 | 10.85
3.3 | Sanitary Waste and Vent | [5 empty] | 3.3 | Sanitary Waste and Vent | [5 empty] | 3.3 | Sanitary Waste and Vent | [5 empty] | 3.3 | Sanitary Waste and Vent | [5 empty] | 3.3 | Sanitary Waste and Vent | [5 empty] | 3.3 | Sanitary Waste and Vent | [5 empty] | 3.3 | Sanitary Waste and Vent | [5 empty] | 3.3 | Sanitary Waste and Vent
b |  | Developer + Either party | 4040 | Tenant | 1040 | 0.42333 | b |  | Developer + Either party | 4040 | Tenant | 1040 | 0.33667 | b |  | Developer + Either Party | 4040 | Tenant | 1040 | 0.84667 | b |  | Developer + Either Party | 4040 | Tenant | 1040 | 1.27 | b |  | Developer + Either Party | 4040 | Tenant | 1040 | 1.27 | b |  | Developer + Either Party | 4040 | Tenant | 1040 | 1.27 | b |  | Developer + Either Party | 1260 | Tenant | 260 | 0.76 | b |  | Developer + Either Party | 4040 | Tenant | 0 | 2.02
3.4 | Grease Waste | [5 empty] | 3.4 | Grease Waste | [5 empty] | 3.4 | Grease Waste | [5 empty] | 3.4 | Grease Waste | [5 empty] | 3.4 | Grease Waste | [5 empty] | 3.4 | Grease Waste | [5 empty] | 3.4 | Grease Waste | [5 empty] | 3.4 | Grease Waste
a |  | Developer + Either party | 2500 | Tenant | 0 | 0.20833 | a |  | Developer + Either Party | N/A | Tenant | N/A | 0 | a |  | Developer + Either Party | N/A | Tenant | N/A | 0 | a |  | Developer + Either Party | N/A | Tenant | N/A | 0 | a |  | Developer | 0 | Tenant + Either party | 2500 | 0.625 | a |  | Developer + Either Party | N/A | Tenant | N/A | 0 | a |  | Developer + Either Party | N/A | Tenant | N/A | 0 | b |  | Developer + Either Party | 0 | Tenant | 50000 | 25
3.5 | Gas | [5 empty] | 3.5 | Gas | [5 empty] | 3.5 | Gas | [5 empty] | 3.5 | Gas | [5 empty] | 3.5 | Gas | [5 empty] | 3.5 | Gas | [5 empty] | 3.5 | Gas | [5 empty] | 3.5 | Gas
a |  | Developer | 5000 | Tenant + Either party | 11000 | 1.3333 | a |  | Developer + Either party | N/A | Tenant | N/A | 0 | a |  | Developer | N/A | Tenant + Either party | N/A | 0 | a |  | Developer | N/A | Tenant + Either party | N/A | 0 | a |  | Developer | 5000 | Tenant + Either party | 11000 | 4 | a |  | Developer | N/A | Tenant + Either party | N/A | 0 | a |  | Developer | N/A | Tenant + Either party | N/A | 0 | a |  | Developer | 5000 | Tenant + Either party | 11000 | 8
Fire Protection Systems | [6 empty] | Fire Protection Systems | [6 empty] | Fire Protection Systems | [6 empty] | Fire Protection Systems | [6 empty] | Fire Protection Systems | [6 empty] | Fire Protection Systems | [6 empty] | Fire Protection Systems | [6 empty] | Fire Protection Systems
3.6 | Wet Sprinkler System | [5 empty] | 3.6 | Wet Sprinkler System | [5 empty] | 3.6 | Wet Sprinkler System | [5 empty] | 3.6 | Wet Sprinkler System | [5 empty] | 3.6 | Wet Sprinkler System | [5 empty] | 3.6 | Wet Sprinkler System | [5 empty] | 3.6 | Wet Sprinkler System | [5 empty] | 3.6 | Wet Sprinkler System
a |  | Developer | 122600 | Tenant + Either party | 0 | 10.2167 | a |  | Developer + Either party | 122600 | Tenant | 0 | 10.2167 | a |  | Developer | 62600 | Tenant + Either party | 0 | 10.4333 | a |  | Developer | 42600 | Tenant + Either party | 0 | 10.65 | a |  | Developer | 42600 | Tenant + Either party | 0 | 10.65 | a |  | Developer | 42600 | Tenant + Either party | 0 | 10.65 | a |  | Developer | 22600 | Tenant + Either party | 0 | 11.3 | a |  | Developer | 22600 | Tenant + Either party | 0 | 11.3
DEVELOPER TOTAL |  |  | 483390 | TENANT TOTAL | 407540 |  | DEVELOPER TOTAL |  |  | 472690 | TENANT TOTAL | 381230 |  | DEVELOPER TOTAL |  |  | 254140 | TENANT TOTAL | 288890 |  | DEVELOPER TOTAL |  |  | 285940 | TENANT TOTAL | 180230 |  | DEVELOPER TOTAL |  |  | 433290 | TENANT TOTAL | 225990 |  | DEVELOPER TOTAL |  |  | 226440 | TENANT TOTAL | 193140 |  | DEVELOPER TOTAL |  |  | 160110 | TENANT TOTAL | 131560 |  | DEVELOPER TOTAL |  |  | 229140 | TENANT TOTAL | 169300
TOTAL |  |  |  | 890930 |  | 74.2442 | TOTAL |  |  |  | 853920 |  | 71.16 | TOTAL |  |  |  | 543030 |  | 90.505 | TOTAL |  |  |  | 466170 |  | 116.5425 | TOTAL |  |  |  | 659280 |  | 164.82 | TOTAL |  |  |  | 419580 |  | 104.895 | TOTAL |  |  |  | 291670 |  | 145.835 | TOTAL |  |  |  | 398440 |  | 199.22
High + 50% |  |  |  | 1336395 |  | 111.3662 | High + 50% |  |  |  | 1280880 |  | 106.74 | High + 50% |  |  |  | 814545 |  | 135.7575 | High + 50% |  |  |  | 699255 |  | 174.8137 | High + 50% |  |  |  | 988920 |  | 247.23 | High + 50% |  |  |  | 629370 |  | 157.3425 | High + 50% |  |  |  | 437505 |  | 218.7525 | High + 50% |  |  |  | 597660 |  | 298.83
Low - 20% |  |  |  | 712744 |  | 59.3953 | Low - 20% |  |  |  | 683136 |  | 56.928 | Low - 20% |  |  |  | 434424 |  | 72.404 | Low - 20% |  |  |  | 372936 |  | 93.234 | Low - 20% |  |  |  | 527424 |  | 131.856 | Low - 20% |  |  |  | 335664 |  | 83.916 | Low - 20% |  |  |  | 233336 |  | 116.668 | Low - 20% |  |  |  | 318752 |  | 159.376

## Design Assumptions <150' Height
Baseline Assumptions
Base Building: |  |  |  |  | Assume buildings are precast plank on block , assume sheetrock and metal frame.
| Tenant Use Type |  |  |  | Supermarket | Cost Allocation |  |  | Pharmacy (Large) | Cost Allocation |  |  | Pharmacy (Small) | Cost Allocation |  |  | Health care Center | Cost Allocation |  |  | Full Service Restaurant | Cost Allocation |  |  | General Retail (Large) | Cost Allocation |  |  | General Retail (Small) | Cost Allocation |  |  | Laundromat | Cost Allocation |  |  | Questions | Rule of thumb
[6 empty] | Developer | Either Party | Tenant |  | Developer | Either Party | Tenant |  | Developer | Either Party | Tenant |  | Developer | Either Party | Tenant |  | Developer | Either Party | Tenant |  | Developer | Either Party | Tenant |  | Developer | Either Party | Tenant |  | Developer | Either Party | Tenant
| Tenant Area (SF) |  |  |  | 12000 |  |  |  | 12000 |  |  |  | 6000 |  |  |  | 4000 |  |  |  | 4000 |  |  |  | 4000 |  |  |  | 2000 |  |  |  | 2000
| Description of Tenant Use and Key Requirements |  |  |  | Supermarket with food prep, refrigeration, etc… | [15 empty] | Kitchen / bar / bathrooms etc… | [11 empty] | 50 wash / 50 dry / bathrooms...?
Base Building Mechanical System
| Base Building Electrical System |  |  |  | 4000 amps, 208Y/120v service, 150kW natural gas generator (life safety only), fire alarm system |  |  |  | 4000 amps, 208Y/120v service, 150kW natural gas generator (life safety only), fire alarm system |  |  |  | 4000 amps, 208Y/120v service, 150kW natural gas generator (life safety only), fire alarm system |  |  |  | 4000 amps, 208Y/120v service, 150kW natural gas generator (life safety only), fire alarm system |  |  |  | 4000 amps, 208Y/120v service, 150kW natural gas generator (life safety only), fire alarm system |  |  |  | 4000 amps, 208Y/120v service, 150kW natural gas generator (life safety only), fire alarm system |  |  |  | 4000 amps, 208Y/120v service, 150kW natural gas generator (life safety only), fire alarm system |  |  |  | 4000 amps, 208Y/120v service, 150kW natural gas generator (life safety only), fire alarm system
| Base Building Plumbing System |  |  |  | Gas Stoves in each unit, 1 bathroom per apt, |  |  |  | Gas Stoves in each unit, 1 bathroom per apt, |  |  |  | Gas Stoves in each unit, 1 bathroom per apt, |  |  |  | Gas Stoves in each unit, 1 bathroom per apt, |  |  |  | Gas Stoves in each unit, 1 bathroom per apt, |  |  |  | Gas Stoves in each unit, 1 bathroom per apt, |  |  |  | Gas Stoves in each unit, 1 bathroom per apt, |  |  |  | Gas Stoves in each unit, 1 bathroom per apt,
| Base Building Fire System |  |  |  | sprinklers |  |  |  | sprinklers |  |  |  | sprinklers |  |  |  | sprinklers |  |  |  | sprinklers |  |  |  | sprinklers |  |  |  | sprinklers |  |  |  | sprinklers
| Base Building |  |  |  | <150' height : 20,000 sf footprint / 12,000 sf retail : 110,000 sf : 130 units : precast plank on block : metal frame and sheetrock |  |  |  | <150' height : 20,000 sf footprint / 12,000 sf retail : 110,000 sf : 130 units : precast plank on block : metal frame and sheetrock |  |  |  | <150' height : 20,000 sf footprint / 12,000 sf retail : 110,000 sf : 130 units : precast plank on block : metal frame and sheetrock |  |  |  | <150' height : 20,000 sf footprint / 12,000 sf retail : 110,000 sf : 130 units : precast plank on block : metal frame and sheetrock |  |  |  | <150' height : 20,000 sf footprint / 12,000 sf retail : 110,000 sf : 130 units : precast plank on block : metal frame and sheetrock |  |  |  | <150' height : 20,000 sf footprint / 12,000 sf retail : 110,000 sf : 130 units : precast plank on block : metal frame and sheetrock |  |  |  | <150' height : 20,000 sf footprint / 12,000 sf retail : 110,000 sf : 130 units : precast plank on block : metal frame and sheetrock |  |  |  | <150' height : 20,000 sf footprint / 12,000 sf retail : 110,000 sf : 130 units : precast plank on block : metal frame and sheetrock
| 1 | Mechanical
| 1.1 | Heating
| a |  | Tenant Air Handling System connection to base building heat source. Needs freeze protection for unleased space | [34 empty] | Rule of thumb 40 - 45btus per sf. Use this to calc the boiler size. Double the btu/sf for rest + laundry
|  |  | 1.1.a.1 |  | Incr. increase in base building heat source; piping from the base building to the unit, metering. (480MBH requires 2" pipe at 20 degree delta; steel pipe 2" to 4" say 300 ft, meter measures flow rate and temp (3 bms points)) | 166500 |  |  | Incr. increase in base building heat source; piping from the base building to the unit, metering. (480 MBH requires 2" pipe at 20 degree delta; steel pipe 2" to 4" say 300 ft, meter measures flow rate and temp (3 bms points)) | 166500 |  |  | Incr. increase in base building heat source; piping from the base building to the unit, metering. (240 MBH requires 1-1/2" pipe at 20 degree delta; steel pipe 1" to 2" say 100 ft, meter measures flow rate and temp (3 bms points)) | 68500 |  |  | Incr. increase in base building heat source; piping from the base building to the unit, metering. (160 MBH requires 1-1/1" pipe at 20 degree delta; steel pipe 1" to 2" say 100 ft, meter measures flow rate and temp (3 bms points)) | 52500 |  |  | Incr. increase in base building heat source; piping from the base building to the unit, metering. (320 MBH requires 2" pipe at 20 degree delta; steel pipe 2" to 4" say 100 ft, meter measures flow rate and temp (3 bms points)) | 92500 |  |  | Incr. increase in base building heat source; piping from the base building to the unit, metering. (160 MBH requires 1-1/2" pipe at 20 degree delta; steel pipe 1" to 2" say 100 ft, meter measures flow rate and temp (3 bms points)) | 47500 |  |  | Incr. increase in base building heat source; piping from the base building to the unit, metering. (80 MBH requires 1" pipe at 20 degree delta; steel pipe 1" to 2" say 100 ft, meter measures flow rate and temp (3 bms points)) | 29500 |  |  | Incr. increase in base building heat source; piping from the base building to the unit, metering. (160 MBH requires 1-1/2" pipe at 20 degree delta; steel pipe 2" to 4" say 100 ft, meter measures flow rate and temp (3 bms points)) | 58500
|  |  | 1.1.a.2 |  | Optional: unit heater for unleased space. Put one per 2000 sf |  | 48000 |  | Optional: unit heater for unleased space. Put one per 2000 sf |  | 48000 |  | Optional: unit heater for unleased space |  | 24000 |  | Optional: unit heater for unleased space |  | 16000 |  | Optional: unit heater for unleased space |  | 16000 |  | Optional: unit heater for unleased space |  | 16000 |  | Optional: unit heater for unleased space |  | 8000 |  | Optional: unit heater for unleased space |  | 8000 |  |  | Say 20 btus for freeze protection
|  |  | 1.1.a.3 |  | Included within AHU line item |  |  | 0 | Included within AHU line item |  |  | 0 | Included within AHU line item |  |  | 0 | Included within AHU line item |  |  | 0 | Included within AHU line item |  |  | 0 | Included within AHU line item |  |  | 0 | Included within AHU line item |  |  | 0 | Included within AHU line item |  |  | 0
| b |  | Condenser water connection to tenant AHU which includes a heat pump. Freeze protection will be required for unleased space
|  |  | 1.1.b.3 | (this item is costed in cooling system) | Incremental increase in condenser water system size, piping from base building to unit, no meter. ( price for condensed water included in cooling system, 40 tons of cooling would be 3" pipe; steel pipe 3" to 4" say 300") Cost here is pipe only | 0 |  |  | Incremental increase in condenser water system size, piping from base building to unit, no meter. ( price for condensed water included in cooling system, 60 tons of cooling would be 4" pipe; steel pipe 3" to 4" say 300") Cost here is pipe only | 0 |  |  | Incremental increase in condenser water system size, piping from base building to unit, no meter. ( price for condensed water included in cooling system, 30 tons of cooling would be 3" pipe; steel pipe 3" to 4" say 300") Cost here is pipe only |  |  |  | Incremental increase in condenser water system size, piping from base building to unit, no meter. ( price for condensed water included in cooling system, 15 tons of cooling would be 2" pipe; steel pipe 3" to 4" say 300") Cost here is pipe only | 0 |  |  | Incremental increase in condenser water system size, piping from base building to unit, no meter. ( price for condensed water included in cooling system, 20 tons of cooling would be 2-1/2" pipe; steel pipe 3" to 4" say 300") Cost here is pipe only | 0 |  |  | Incremental increase in condenser water system size, piping from base building to unit, no meter. ( price for condensed water included in cooling system, 16 tons of cooling would be 2" pipe; steel pipe 3" to 4" say 300") Cost here is pipe only | 0 |  |  | Incremental increase in condenser water system size, piping from base building to unit, no meter. ( price for condensed water included in cooling system, 8 tons of cooling would be 1-1/2" pipe; steel pipe 3" to 4" say 300") Cost here is pipe only | 0 |  |  | Incremental increase in condenser water system size, piping from base building to unit, no meter. ( price for condensed water included in cooling system, 8 tons of cooling would be 1-1/2" pipe; steel pipe 3" to 4" say 300") Cost here is pipe only | 0 |  |  |  | assuming 3 gmp/ton
|  |  | 1.1.b.2 |  | Optional: Electric unit heaters for unleased space so sprinkler pipes do not freeze |  | 48000 |  |  |  | 0 | [7 empty] | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
|  |  | 1.1.b.3 |  | Included within AHU line item |  |  | 0 |  |  |  | 0 | [7 empty] | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
| c |  | Steam connection from base buildings service. Service metered by landlord
|  |  | 1.1.c.1 | update pipe sizes across row | Incremental increase in steam system size, piping from base building to unit, meter. (assume 2" steam pipe, 2" condensate returns, steam trap, meter is 2 bms points that measures condensate volume) | 58000 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
|  |  | 1.1.c.2 |  | Optional: Steam fired unit heaters |  | 5000 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
1.1.c.3
| d |  | Tenant provides boiler themselves: Needs gas service connection, combustion air make-up, and boiler flue.
|  |  | 1.1.d.1 | update pipe sizes across row | Incremental increase in gas system, piping from base building to unit, 1" gas pipe, meter 1 bms point, flue stainless steel exit roof, needs a dedicated shaft 18" x 18" od) | 12500 |  |  | Incremental increase in gas system, piping from base building to unit, 1" gas pipe, meter 1 bms point, flue stainless steel exit roof, needs a dedicated shaft 18" x 18" od) | 12500 |  |  | Incremental increase in gas system, piping from base building to unit, 1" gas pipe, meter 1 bms point, flue stainless steel exit roof, needs a dedicated shaft 18" x 18" od) | 12500 |  |  | Incremental increase in gas system, piping from base building to unit, 1" gas pipe, meter 1 bms point, flue stainless steel exit roof, needs a dedicated shaft 18" x 18" od) | 12500 |  |  | Incremental increase in gas system, piping from base building to unit, 1" gas pipe, meter 1 bms point, flue stainless steel exit roof, needs a dedicated shaft 18" x 18" od) | 12500 |  |  | Incremental increase in gas system, piping from base building to unit, 1" gas pipe, meter 1 bms point, flue stainless steel exit roof, needs a dedicated shaft 18" x 18" od) | 12500 |  |  | Incremental increase in gas system, piping from base building to unit, 1" gas pipe, meter 1 bms point, flue stainless steel exit roof, needs a dedicated shaft 18" x 18" od) | 12500 |  |  | Incremental increase in gas system, piping from base building to unit, 1" gas pipe, meter 1 bms point, flue stainless steel exit roof, needs a dedicated shaft 18" x 18" od) | 12500
|  |  | 1.1.d.2 |  | Boiler |  | 96000 |  | Boiler |  | 96000 |  | Boiler |  | 48000 |  | Boiler |  | 32000 |  | Boiler |  | 64000 |  | Boiler |  | 32000 |  | Boiler |  | 16000 |  | Boiler |  | 32000 |  |  | Rule of thumb 40 - 45btus per sf. Use this to calc the boiler size. Double the btu/sf for rest + laundry
|  |  | 1.1.d.3 |  | Boiler |  |  | 0 | Boiler |  |  | 0 | Boiler |  |  | 0 | Boiler |  |  | 0 | Boiler |  |  | 0 | Boiler |  |  | 0 | Boiler |  |  | 0 | Boiler |  |  | 0
| 1.2 | Cooling
| a |  | Connect tenants AHU to base building chiller or heat pump, which includes chilled-water coil. Chiller/heat pump needs to be sized appropriately
|  |  | 1.2.a.1 | update pipe sizes across row | Incr. increase in base building cooling source; piping from the base building to the unit, metering. (40 tons requires 2-1/2" pipe at 14 degree delta; steel pipe 4" to 6", say 300 ft, meter measures flow rate and temp 3 bms points) | 100500 |  |  | Incr. increase in base building cooling source; piping from the base building to the unit, metering. (60 tons requires 3" pipe at 14 degree delta; steel pipe 4" to 6", say 300 ft, meter measures flow rate and temp 3 bms points) | 106500 |  |  | Incr. increase in base building cooling source; piping from the base building to the unit, metering. (30 tons requires 2-1/2" pipe at 14 degree delta; steel pipe 4" to 6", say 300 ft, meter measures flow rate and temp 3 bms points) | 100500 |  |  | Incr. increase in base building cooling source; piping from the base building to the unit, metering. (15 tons requires 2" pipe at 14 degree delta; steel pipe 4" to 6", say 300 ft, meter measures flow rate and temp 3 bms points) | 94500 |  |  | Incr. increase in base building cooling source; piping from the base building to the unit, metering. (20 tons requires 2" pipe at 14 degree delta; steel pipe 4" to 6", say 300 ft, meter measures flow rate and temp 3 bms points) | 94500 |  |  | Incr. increase in base building cooling source; piping from the base building to the unit, metering. (16 tons requires 2" pipe at 14 degree delta; steel pipe 4" to 6", say 300 ft, meter measures flow rate and temp 3 bms points) | 94500 |  |  | Incr. increase in base building cooling source; piping from the base building to the unit, metering. (8 tons requires 1-1/4" pipe at 14 degree delta; steel pipe 4" to 6", say 300 ft, meter measures flow rate and temp 3 bms points) | 85500 |  |  | Incr. increase in base building cooling source; piping from the base building to the unit, metering. (8 tons requires 1-1/4" pipe at 14 degree delta; steel pipe 4" to 6", say 300 ft, meter measures flow rate and temp 3 bms points) | 85500
|  |  | 1.2.a.2 |  | N/A |  |  |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0
|  |  | 1.2.a.3 |  | Included within AHU line item |  |  | 0 | Included within AHU line item |  |  | 0 | Included within AHU line item |  |  | 0 | Included within AHU line item |  |  | 0 | Included within AHU line item |  |  | 0 | Included within AHU line item |  |  | 0 | Included within AHU line item |  |  | 0 | Included within AHU line item |  |  | 0
| b |  | Base building provides condenser water with heat pump. Loop includes cooling tower. Potential electric service upgrade
|  |  | 1.2.b.1 | update pipe sizes across row | Incremental increase in condenser water system size, piping from base building to unit, no meter. ( price for condensed water included in cooling system, 40 tons of cooling would be 3" pipe; steel pipe 3" to 4" say 300") Cost here is pipe only | 75000 |  |  | Incremental increase in condenser water system size, piping from base building to unit, no meter. ( price for condensed water included in cooling system, 60 tons of cooling would be 4" pipe; steel pipe 3" to 4" say 300") Cost here is pipe only | 96000 |  |  | Incremental increase in condenser water system size, piping from base building to unit, no meter. ( price for condensed water included in cooling system, 30 tons of cooling would be 3" pipe; steel pipe 3" to 4" say 300") Cost here is pipe only | 75000 |  |  | Incremental increase in condenser water system size, piping from base building to unit, no meter. ( price for condensed water included in cooling system, 15 tons of cooling would be 2" pipe; steel pipe 3" to 4" say 300") Cost here is pipe only | 63000 |  |  | Incremental increase in condenser water system size, piping from base building to unit, no meter. ( price for condensed water included in cooling system, 20 tons of cooling would be 2-1/2" pipe; steel pipe 3" to 4" say 300") Cost here is pipe only | 69000 |  |  | Incremental increase in condenser water system size, piping from base building to unit, no meter. ( price for condensed water included in cooling system, 16 tons of cooling would be 2" pipe; steel pipe 3" to 4" say 300") Cost here is pipe only |  |  |  | Incremental increase in condenser water system size, piping from base building to unit, no meter. ( price for condensed water included in cooling system, 8 tons of cooling would be 1-1/2" pipe; steel pipe 3" to 4" say 300") Cost here is pipe only | 54000 |  |  | Incremental increase in condenser water system size, piping from base building to unit, no meter. ( price for condensed water included in cooling system, 8 tons of cooling would be 1-1/2" pipe; steel pipe 3" to 4" say 300") Cost here is pipe only | 54000
|  |  | 1.2.b.2 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0
|  |  | 1.2.b.3 |  | Included within AHU line item |  |  | 0 | Included within AHU line item |  |  | 0 | Included within AHU line item |  |  | 0 | Included within AHU line item |  |  | 0 | Included within AHU line item |  |  | 0 | Included within AHU line item |  | 0 | 0 | Included within AHU line item |  |  | 0 | Included within AHU line item |  |  | 0
| c |  | VRF Cooling System (Variable Refrigerant Flow), assuming building has a refrigerant system available. Provide a connection point for refrigeration to tenants AHU that includes a VRF Cooling Coil.
|  |  | 1.2.c.1 | update pipe sizes across row | Dedicated shaft for refrig pipe | 0 |  |  | Dedicated shaft for refrig pipe | 0 |  |  | Dedicated shaft for refrig pipe | 0 |  |  | Dedicated shaft for refrig pipe | 0 |  |  | Dedicated shaft for refrig pipe | 0 |  |  | Dedicated shaft for refrig pipe | 0 |  |  | Dedicated shaft for refrig pipe | 0 |  |  | Dedicated shaft for refrig pipe | 0
|  |  | 1.2.c.2 |  | Rooftop Condenser Unit, refrigerant piping from unit to roof, 1" copper pipe, length is height of building |  | 67500 |  | Rooftop Condenser Unit, refrigerant piping from unit to roof, 1" copper pipe, length is height of building |  | 67500 |  | Rooftop Condenser Unit, refrigerant piping from unit to roof, 1" copper pipe, length is height of building |  | 67500 |  | Rooftop Condenser Unit, refrigerant piping from unit to roof, 1" copper pipe, length is height of building |  | 67500 |  | Rooftop Condenser Unit, refrigerant piping from unit to roof, 1" copper pipe, length is height of building |  | 67500 |  | Rooftop Condenser Unit, refrigerant piping from unit to roof, 1" copper pipe, length is height of building |  | 67500 |  | Rooftop Condenser Unit, refrigerant piping from unit to roof, 1" copper pipe, length is height of building |  | 67500 |  | Rooftop Condenser Unit, refrigerant piping from unit to roof, 1" copper pipe, length is height of building |  | 67500
|  |  | 1.2.c.3 |  | Evaporator included in AHU line item |  |  | 0 | Evaporator included in AHU line item |  |  | 0 | Evaporator included in AHU line item |  |  | 0 | Evaporator included in AHU line item |  |  | 0 | Evaporator included in AHU line item |  |  | 0 | Evaporator included in AHU line item |  |  | 0 | Evaporator included in AHU line item |  |  | 0 | Evaporator included in AHU line item |  |  | 0
| d |  | DX cooling system that includes a refrigerant cooling coil and an external rooftop condenser unit, refrigerant piping and electric conduit.
|  |  | 1.2.d.1 | update pipe sizes across row | Dedicated shat for refrig pipe | 0 |  |  | Dedicated shat for refrig pipe | 0 |  |  | Dedicated shat for refrig pipe | 0 |  |  | Dedicated shat for refrig pipe | 0 |  |  | Dedicated shat for refrig pipe | 0 |  |  | Dedicated shat for refrig pipe | 0 |  |  | Dedicated shat for refrig pipe | 0 |  |  | Dedicated shat for refrig pipe | 0
|  |  | 1.2.d.2 |  | Rooftop Condenser Unit, refrigerant piping from unit to roof, 1" copper pipe, length is height of building |  | 67500 |  | Rooftop Condenser Unit, refrigerant piping from unit to roof, 1" copper pipe, length is height of building |  | 67500 |  | Rooftop Condenser Unit, refrigerant piping from unit to roof, 1" copper pipe, length is height of building |  | 67500 |  | Rooftop Condenser Unit, refrigerant piping from unit to roof, 1" copper pipe, length is height of building |  | 67500 |  | Rooftop Condenser Unit, refrigerant piping from unit to roof, 1" copper pipe, length is height of building |  | 67500 |  | Rooftop Condenser Unit, refrigerant piping from unit to roof, 1" copper pipe, length is height of building |  | 67500 |  | Rooftop Condenser Unit, refrigerant piping from unit to roof, 1" copper pipe, length is height of building |  | 67500 | 67500 | Rooftop Condenser Unit, refrigerant piping from unit to roof, 1" copper pipe, length is height of building |  | 67500
|  |  | 1.2.d.3 |  | Evaporator included in AHU line item |  |  | 0 | Evaporator included in AHU line item |  |  | 0 | Evaporator included in AHU line item |  |  | 0 | Evaporator included in AHU line item |  |  | 0 | Evaporator included in AHU line item |  |  | 0 | Evaporator included in AHU line item |  |  | 0 | Evaporator included in AHU line item |  |  |  | Evaporator included in AHU line item |  |  | 0
| e |  | DX cooling system integrated in tenant ceiling mounted AHU including a refrigerant cooling coil, with condenser section separately ducted to the outside
|  |  | 1.2.e.1 | See small retail option | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0
|  |  | 1.2.e.2 |  | N/A |  |  |  | N/A |  |  |  | N/A |  |  |  | N/A |  |  |  | N/A |  |  |  | N/A |  |  |  | N/A |  |  |  | N/A
|  |  | 1.2.e.3 |  | N/A |  |  |  | N/A |  |  |  | N/A |  |  |  | N/A |  |  |  | N/A |  |  |  | N/A |  |  |  | Evaporator and Condenser included in AHU line item |  |  |  | N/A
| 1.3 | Ventilation
| a |  | Air intakes and exhaust that connect to tenant AHU in ceiling, roof above retail unit, or in a space in the rear of retail unit.
|  |  | 1.3.a.1 |  | Minimum 2.88 SF free area Louver | 6000 |  |  | Minimum 5.52 SF free area Louver | 9000 |  |  | Minimum 2.76 SF free area Louver | 4000 |  |  | Minimum 1.84 SF free area Louver | 1500 |  |  | Minimum 2.82 SF free area Louver | 63000 |  |  | Minimum 1.86 SF free area Louver | 2000 |  |  | Minimum 0.93 SF free area Louver | 1000 | 1000 |  | Minimum 0.84 SF free area Louver | 2000 | 2000
|  |  | 1.3.a.2 |  | Ducting from louver to AH |  | 60000 |  | Ducting from louver to AH |  | 60000 |  | Ducting from louver to AH |  | 60000 |  | Ducting from louver to AH |  | 60000 |  | Ducting from louver to AH |  | 0 |  | Ducting from louver to AH |  | 60000 |  | Ducting from louver to AH |  | 60000 | 60000 | Ducting from louver to AH |  | 60000 | 60000
|  |  | 1.3.a.3 | Need to research cost deltas on AHU types (DX vs. Cooling/ Heat coil, see if there is a material difference) | AHU (includes: filters, mixing section, heating coil, cooling coil, fan, return fan, dist. duct work, grills, for spaces bigger than 4000sf have vav boxes) |  |  | 0 | AHU (includes: filters, mixing section, heating coil, cooling coil, fan, return fan, dist. duct work, grills, for spaces bigger than 4000sf have vav boxes) |  |  | 0 | AHU (includes: filters, mixing section, heating coil, cooling coil, fan, return fan, dist. duct work, grills, for spaces bigger than 4000sf have vav boxes) |  |  | 0 | AHU (includes: filters, mixing section, heating coil, cooling coil, fan, return fan, dist. duct work, grills, for spaces bigger than 4000sf have vav boxes) |  |  | 0 | AHU (includes: filters, mixing section, heating coil, cooling coil, fan, return fan, dist. duct work, grills, for spaces bigger than 4000sf have vav boxes) |  |  | 0 | AHU (includes: filters, mixing section, heating coil, cooling coil, fan, return fan, dist. duct work, grills, for spaces bigger than 4000sf have vav boxes) |  |  | 0 | AHU (includes: filters, heating coil, dx cooling coil, supply fan only, ducts from condenser to louvers) |  |  | 0 | AHU (includes: filters, heating coil, dx cooling coil, supply fan only, ducts from condenser to louvers) |  |  | 0
| 1.4 | Air-Side Economizers
| a |  | 5000 cfm (1cfm/sf for all retail space)
|  |  | 1.4.a.1 |  | In AHU item | 0 |  |  | In AHU item | 0 |  |  | In AHU item | 0 |  |  | In AHU item | 0 |  |  | In AHU item | 0 |  |  | In AHU item | 0 |  |  | In AHU item | 0 |  |  | In AHU item | 0
|  |  | 1.4.a.2 |  | In AHU item |  | 0 |  | In AHU item |  | 0 |  | In AHU item |  |  |  | In AHU item |  |  |  | In AHU item |  |  |  | In AHU item |  |  |  | In AHU item |  |  |  | In AHU item
|  |  | 1.4.a.3 |  | In AHU item |  |  | 0 | In AHU item |  |  | 0 | In AHU item |  |  | 0 | In AHU item |  |  | 0 | In AHU item |  |  | 0 | In AHU item |  |  | 0 | In AHU item |  |  | 0 | In AHU item |  |  | 0
| 1.5 | Exhaust Air
| a |  | Exhaust air duct vent and fans.
|  |  | 1.5.a.1 | For tenant use only 200 cfm, public use 600 cfm | Every space needs toilet exhaust fan, landlord provide louver, both tenant and public restrooms | 6000 |  |  | Every space needs toilet exhaust fan, landlord provide louver | 6000 |  |  | Every space needs toilet exhaust fan, landlord provide louver | 6000 |  |  | Every space needs toilet exhaust fan, landlord provide louver | 6000 |  |  | Every space needs toilet exhaust fan, landlord provide louver | 12000 |  |  | Every space needs toilet exhaust fan, landlord provide louver | 6000 |  |  | Every space needs toilet exhaust fan, landlord provide louver | 6000 |  |  | Every space needs toilet exhaust fan, landlord provide louver | 0
|  |  | 1.5.a.2 |  | Duct from louver to fan, fan |  | 11000 |  | Duct from louver to fan, fan |  | 11000 |  | Duct from louver to fan, fan |  | 11000 |  | Duct from louver to fan, fan |  | 11000 |  | Duct from louver to fan, fan |  | 22000 |  | Duct from louver to fan, fan |  | 11000 |  | Duct from louver to fan, fan |  | 11000 |  | Duct from louver to fan, fan |  | 0
|  |  | 1.5.a.3 |  | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0
| 1.6 | Kitchen Exhaust
| a |  | Kitchen and dishwasher exhaust vents and fans.
|  |  | 1.6.a.1 |  | Provide shaft, louvers | 1500 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | Provide shaft, louvers | 1600 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0
|  |  | 1.6.a.2 |  | Kitchen exhaust fan, |  | 10000 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | Kitchen exhaust fan, |  | 10000 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0
|  |  | 1.6.a.3 |  | Exhaust hood |  |  | 15000 | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0 | Exhaust hood |  |  | 15000 | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0
| 1.7 | Air-Handling Units
| a |  | Tenant owned, ceiling-mounted, single or two zone in retail space with louvered connections to outside. Independent controlled exhaust fans for bathrooms. For retail space less than 4000sf
|  |  | 1.7.a.1 |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0
|  |  | 1.7.a.2 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0
|  |  | 1.7.a.3 |  | ~1.3 CFM/SF, then research diff AHU types / costs, (single vs multi zones, inside vs outside), these are defined above |  |  | #N/A | ~2 CFM/SF, then research diff AHU types / costs, (single vs multi zones, inside vs outside), these are defined above |  |  | 90190 | ~2 CFM/SF, then research diff AHU types / costs, (single vs multi zones, inside vs outside), these are defined above |  |  | 46250 | ~1.5 CFM/SF, then research diff AHU types / costs, (single vs multi zones, inside vs outside), these are defined above |  |  | 27500 | ~2 CFM/SF, then research diff AHU types / costs, (single vs multi zones, inside vs outside), these are defined above |  |  | 35000 | ~1.6 CFM/SF, then research diff AHU types / costs, (single vs multi zones, inside vs outside), these are defined above |  |  | 27500 | ~1.6 CFM/SF, then research diff AHU types / costs, (single vs multi zones, inside vs outside), these are defined above |  |  | 19000 | ~1.6 CFM/SF, then research diff AHU types / costs, (single vs multi zones, inside vs outside), these are defined above |  |  | 19000
| b |  | Tenant owned, ceiling-mounted, single or two zone in retail space with connection to outside at roof level or in rear yard. Ducts will serve multiple retail units. Independent controlled exhaust fans for bathrooms. Additional space required for ducts to run through residential space.
|  |  | 1.7.b.1 |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0
|  |  | 1.7.b.2 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 | 0
|  |  | 1.7.b.3 |  | ~1.3 CFM/SF, then research diff AHU types / costs, (single vs multi zones, inside vs outside), these are defined above |  |  | #N/A | ~2 CFM/SF, then research diff AHU types / costs, (single vs multi zones, inside vs outside), these are defined above |  |  | 90190 | ~2 CFM/SF, then research diff AHU types / costs, (single vs multi zones, inside vs outside), these are defined above |  |  | 46250 | ~1.5 CFM/SF, then research diff AHU types / costs, (single vs multi zones, inside vs outside), these are defined above |  |  | 27500 | ~2 CFM/SF, then research diff AHU types / costs, (single vs multi zones, inside vs outside), these are defined above |  |  | 35000 | ~1.6 CFM/SF, then research diff AHU types / costs, (single vs multi zones, inside vs outside), these are defined above |  |  | 27500 | ~1.6 CFM/SF, then research diff AHU types / costs, (single vs multi zones, inside vs outside), these are defined above |  |  | 19000 | ~1.6 CFM/SF, then research diff AHU types / costs, (single vs multi zones, inside vs outside), these are defined above
| c |  | Tenant owned, roof mounted, multi-zone AHU above retail unit. Outside air connections are made directly into the AHU.
|  |  | 1.7.c.1 |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0
|  |  | 1.7.c.2 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0
|  |  | 1.7.c.3 |  | ~1.3 CFM/SF, then research diff AHU types / costs, (single vs multi zones, inside vs outside), these are defined above |  |  | #N/A | ~2 CFM/SF, then research diff AHU types / costs, (single vs multi zones, inside vs outside), these are defined above |  |  | 90190 | ~2 CFM/SF, then research diff AHU types / costs, (single vs multi zones, inside vs outside), these are defined above |  |  | 46250 | ~1.5 CFM/SF, then research diff AHU types / costs, (single vs multi zones, inside vs outside), these are defined above |  |  | 27500 | ~2 CFM/SF, then research diff AHU types / costs, (single vs multi zones, inside vs outside), these are defined above |  |  | 35000 | ~1.6 CFM/SF, then research diff AHU types / costs, (single vs multi zones, inside vs outside), these are defined above |  |  | 27500 | ~1.6 CFM/SF, then research diff AHU types / costs, (single vs multi zones, inside vs outside), these are defined above |  |  | 19000 | ~1.6 CFM/SF, then research diff AHU types / costs, (single vs multi zones, inside vs outside), these are defined above |  |  | 19000
| d |  | Single or multi zone AHU mounted in mechanical room to rear of the retail space or above a storage space. Fresh air intake from rear yard or roof
|  |  | 1.7.d.1 |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0
|  |  | 1.7.d.2 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0
|  |  | 1.7.d.3 |  | ~1.3 CFM/SF, then research diff AHU types / costs, (single vs multi zones, inside vs outside), these are defined above |  |  | #N/A | ~2 CFM/SF, then research diff AHU types / costs, (single vs multi zones, inside vs outside), these are defined above |  |  | 90190 | ~2 CFM/SF, then research diff AHU types / costs, (single vs multi zones, inside vs outside), these are defined above |  |  | 46250 | ~1.5 CFM/SF, then research diff AHU types / costs, (single vs multi zones, inside vs outside), these are defined above |  |  | 27500 | ~2 CFM/SF, then research diff AHU types / costs, (single vs multi zones, inside vs outside), these are defined above |  |  | 35000 | ~1.6 CFM/SF, then research diff AHU types / costs, (single vs multi zones, inside vs outside), these are defined above |  |  | 27500 | ~1.6 CFM/SF, then research diff AHU types / costs, (single vs multi zones, inside vs outside), these are defined above |  |  | 19000 | ~1.6 CFM/SF, then research diff AHU types / costs, (single vs multi zones, inside vs outside), these are defined above |  |  | 19000
| 1.8 | Intakes and Exhaust
| a |  | Intake and Exhaust louvers in the street face of retail unit. If cooling option 3C is in use, additional louver area will be required
|  |  | 1.8.a.1 |  | Minimum 2.88 SF free area Louver (each) | 6000 |  |  | Minimum 5.52 SF free area Louver (each) |  |  |  | Minimum 2.76 SF free area Louver (each) | 4000 |  |  | Minimum 1.84 SF free area Louver (each) | 1500 |  |  | Minimum 2.82 SF free area Louver (each) | 3000 |  |  | Minimum 1.86 SF free area Louver (each) |  | 2000 |  | Minimum 0.93 SF free area Louver (each) | 1000 |  |  | Minimum 0.84 SF free area Louver (each) | 2000
|  |  | 1.8.a.2 |  | N/A |  | 0 |  | N/A |  |  |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  |  | 0 | N/A |  | 0 |  | N/A |  | 0
|  |  | 1.8.a.3 |  | N/A |  |  | 0 | N/A |  |  |  | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  |  | N/A |  |  | 0 | N/A |  |  | 0
| b |  | Intake and Exhaust at roof level, serving multiple retail units
|  |  | 1.8.b.1 |  | Goose neck at the roof, duct through shaft to unit (Eric to define size) | 65000 |  |  | Goose neck at the roof, duct through shaft to unit (Eric to define size) |  |  |  | Goose neck at the roof, duct through shaft to unit (Eric to define size) | 65000 |  |  | Goose neck at the roof, duct through shaft to unit (Eric to define size) | 65000 |  |  | Goose neck at the roof, duct through shaft to unit (Eric to define size) | 65000 |  |  | Goose neck at the roof, duct through shaft to unit (Eric to define size) | 65000 |  |  | Goose neck at the roof, duct through shaft to unit (Eric to define size) | 65000 |  |  | Probably not an option as dryer exhaust is typically pretty limited on how far it can run. | 0
|  |  | 1.8.b.2 |  | N/A |  | 0 |  | N/A |  |  |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0
|  |  | 1.8.b.3 |  | N/A |  |  | 0 | N/A |  |  |  | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0
| 2 | Electrical - Carl to check whole section
| 2.1 | Separate metering for electricity by utility
| a |  | Dedicated Con Edison service to retail space, or from a dedicated service switch from base building. Install wire, conduit, excavations, and any Con Ed costs
|  |  | 2.1.a.1 |  | 800 amp, 208Y/120v three phase electrical service. Assume Con Edison will cover cost for new incoming service. Landlord to provide 800 amp CT Cabinet and 800 amp service switch in tenant space | New service | N/A | N/A | 400 amp (Carl to check size), 208Y/120v three phase electrical service. Assume Con Edison will cover cost for new incoming service. Landlord to provide 400 amp CT Cabinet and 400 amp service switch in tenant space, | 6850 |  |  | Assuming gas kitchen. 200 amp (Carl to check size), 208Y/120v three phase electrical service. Assume Con Edison will cover cost for new incoming service. Landlord to provide 200 amp CT Cabinet and 200 amp service switch in tenant space, | 3300 |  |  | 150 amp, 208Y/120v three phase electrical service. Assume Con Edison will cover cost for new incoming service. Landlord to provide 150 amp CT Cabinet and 150 amp service switch in tenant space, | 3300 |  |  | Assuming gas kitchen. 400 amp, 208Y/120v three phase electrical service. Assume Con Edison will cover cost for new incoming service. Landlord to provide 400 amp CT Cabinet and 400 amp service switch in tenant space, | 6850 |  |  | 200 amp (Carl to check size), 208Y/120v three phase electrical service. Assume Con Edison will cover cost for new incoming service. Landlord to provide 200 amp CT Cabinet and 200 amp service switch in tenant space, | 3300 |  |  | 100 amp (Carl to check size), 208Y/120v three phase electrical service. Assume Con Edison will cover cost for new incoming service. Landlord to provide 100 amp CT Cabinet and 100 amp service switch in tenant space, | 2750 |  |  | 200 amp (Carl to check size), 208Y/120v three phase electrical service. Assume Con Edison will cover cost for new incoming service. Landlord to provide 200 amp CT Cabinet and 200 amp service switch in tenant space, | 3300
|  |  | 2.1.a.2 |  | N/A | [5 empty] | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0
|  |  | 2.1.a.3 |  | Branch circuiting | N/A | N/A | All branch circuiting |  |  |  | 1000 |  |  |  | 1000 |  |  |  | 1000 |  |  |  | 1000 |  |  |  | 1000 |  |  |  | 1000 |  |  |  | 1000
| b |  | Connect retail units to base building electrical service and provide sub-meter. Install all conduit, wire, excavation, and Con Ed Costs.
|  |  | 2.1.b.1 |  | Use spare 800 amp switch in base building switchboard. Install (2) sets of (4) 500kcm + (1)#1/0g in 3 1/2" c 100' to tenant space. Install 800 amp disconnect switch in tenant space. Landlord will need to upsize incoming electrical service to accommodate, sub-meter | Landloard installs conductors from base building switchboard to tenenat space and provides 800 map switch in tenant space. | N/A | N/A | Use spare 400 amp switch in base building switchboard. Install (1) sets of (4) 500kcm + (1)#1/0g in 3 1/2" c 100' to tenant space. Install 400 amp disconnect switch in tenant space. Landlord will need to upsize incoming electrical service to accommodate, sub-meter | 14700 |  |  | Use spare 200 amp switch in base building switchboard. Install (1) sets of (4) 3/0 + (1)#2g in 2 1/2" c 100' to tenant space. Install 200 amp disconnect switch in tenant space. Landlord will need to upsize incoming electrical service to accommodate, sub-meter | 7450 |  |  | Use spare 150 amp switch in base building switchboard. Install (1) sets of (4) 1/0 + (1)#6G in 2" c 100' to tenant space. Install 150 amp disconnect switch in tenant space. Landlord will need to upsize incoming electrical service to accommodate, sub-meter | 6450 |  |  | Use spare 400 amp switch in base building switchboard. Install (1) set of (4) 500kcm + (1)#1/0g in 3 1/2" c 100' to tenant space. Install 400 amp disconnect switch in tenant space. Landlord will need to upsize incoming electrical service to accommodate, sub-meter | 9700 |  |  | Use spare 200 amp switch in base building switchboard. Install (1) sets of (4) 3/0 + (1)#2g in 2 1/2" c 100' to tenant space. Install 200 amp disconnect switch in tenant space. Landlord will need to upsize incoming electrical service to accommodate, sub-meter | 7450 |  |  | Use spare 100 amp switch in base building switchboard. Install (1) sets of (4) #1 + (1)#6g in 1 1/2" c 100' to tenant space. Install 100 amp disconnect switch in tenant space. Landlord will need to upsize incoming electrical service to accommodate, sub-meter | 6200 |  |  | Use spare 200 amp switch in base building switchboard. Install (1) sets of (4) 3/0 + (1)#2g in 2 1/2" c 100' to tenant space. Install 200 amp disconnect switch in tenant space. Landlord will need to upsize incoming electrical service to accommodate, sub-meter | 7450
|  |  | 2.1.b.2 |  | N/A |  |  |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0
|  |  | 2.1.b.3 |  | Branch circuiting | N/A | N/A | All branch circuiting | Branch circuiting |  |  | 1000 | Branch circuiting |  |  | 1000 | Branch circuiting |  |  | 1000 | Branch circuiting |  |  | 1000 | Branch circuiting |  |  | 1000 | Branch circuiting |  |  | 1000 | Branch circuiting |  |  | 1000
| 2.2 | Emergency Power
| a |  | Emergency lights and signage; provided by tenant
|  |  | 2.2.a.1 |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0
|  |  | 2.2.a.2 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0
|  |  | 2.2.a.3 |  | Emergency lights by tenant, Tenant to provide fixture with intergal 90 minute battery packs |  |  | 1200 | Emergency lights by tenant, Tenant to provide fixture with intergal 90 minute battery packs |  |  | 1200 | Emergency lights by tenant, Tenant to provide fixture with intergal 90 minute battery packs |  |  | 600 | Emergency lights by tenant, Tenant to provide fixture with intergal 90 minute battery packs |  |  | 450 | Emergency lights by tenant, Tenant to provide fixture with intergal 90 minute battery packs |  |  | 450 | Emergency lights by tenant, Tenant to provide fixture with intergal 90 minute battery packs |  |  | 600 | Emergency lights by tenant, Tenant to provide fixture with intergal 90 minute battery packs |  |  | 300 | Emergency lights by tenant, Tenant to provide fixture with intergal 90 minute battery packs |  |  | 300
| b |  | Backup generator for supermarket space
|  |  | 2.2.b.1 |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0
|  |  | 2.2.b.2 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0
|  |  | 2.2.b.3 | Check with Carl | assume all costs for generator is by tenant. Will require new gas service. Assume tenant will pay for new gas service. Assume a 15kw natural gas generator with 60 amp switch to serve emergency distribution within tenant space. | N/A | N/A | 26000 | assume all costs for generator is by tenant. Will require new gas service. Assume tenant will pay for new gas service. Assume a 10kw natural gas generator with 30 amp switch to serve emergency distribution within tenant space. |  |  | 21000 | assume all costs for generator is by tenant. Will require new gas service. Assume tenant will pay for new gas service. Assume a 5kw natural gas generator with 15 amp switch to serve emergency distribution within tenant space. |  |  | 10340 | assume all costs for generator is by tenant. Will require new gas service. Assume tenant will pay for new gas service. Assume a 3.5kw natural gas generator with 15 amp switch to serve emergency distribution within tenant space. |  |  | 9650 | assume all costs for generator is by tenant. Will require new gas service. Assume tenant will pay for new gas service. Assume a 10kw natural gas generator with 30 amp switch to serve emergency distribution within tenant space. |  |  | 21000 | assume all costs for generator is by tenant. Will require new gas service. Assume tenant will pay for new gas service. Assume a 5kw natural gas generator with 20 amp switch to serve emergency distribution within tenant space. |  |  | 10340 | assume all costs for generator is by tenant. Will require new gas service. Assume tenant will pay for new gas service. Assume a 2.5kw natural gas generator with 15 amp switch to serve emergency distribution within tenant space. |  |  | 9000 | assume all costs for generator is by tenant. Will require new gas service. Assume tenant will pay for new gas service. Assume a 5kw natural gas generator with 20 amp switch to serve emergency distribution within tenant space. |  |  | 10340
| c |  | Connection to base buildings backup power: Assume life safety loads only will require emergency power in tenant space. Assume emergency lights and fire alarm only.
|  |  | 2.2.c.1 |  | Assume 15kw worth of emergency power. Landlord to install (4) #4 + (1) #8 g in 1 1/4"c 100' into tenant space and terminate in a 60a 3 pole disconnect switch in tenant's space. | Lanlorad install feeder and 30 amp switch to tenant space | N/A | N/A | Assume 10kw worth of emergency power. Landlord to install (4) #10 + (1) #12 g in 1"c 100' into tenant space and terminate in a 30a 3 pole disconnect switch in tenant's space. | 23000 |  |  | Assume 5kw worth of emergency power. Landlord to install (4) #10 + (1) #2 g in 1"c 100' into tenant space and terminate in a 20a 3 pole disconnect switch in tenant's space. | 13340 |  |  | Assume 3.5kw worth of emergency power. Landlord to install (4) #10 + (1) #2 g in 1"c 100' into tenant space and terminate in a 15a 3 pole disconnect switch in tenant's space. | 12650 |  |  | Assume 10kw worth of emergency power. Landlord to install (4) #10 + (1) #2 g in 1"c 100' into tenant space and terminate in a 30a 3 pole disconnect switch in tenant's space. | 24000 |  |  | Assume 5kw worth of emergency power Landlord to install (4) #10 + (1) #2 g in 1"c 100' into tenant space and terminate in a 20a 3 pole disconnect switch in tenant's space. | 13340 | 13340 |  | Assume 2.5kw worth of emergency power Landlord to install (4) #10 + (1) #2 g in 1"c 100' into tenant space and terminate in a 15a 3 pole disconnect switch in tenant's space. | 12000 |  |  | Assume 5kw worth of emergency power. Landlord to install (4) #10 + (1) #2 g in 1"c 100' into tenant space and terminate in a 20a 3 pole disconnect switch in tenant's space. | 13340
|  |  | 2.2.c.2 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0
|  |  | 2.2.c.3 |  | Branch circuiting | N/A | N/A | By Tenant | Branch circuiting |  |  | 1000 | Branch circuiting |  |  | 1000 | Branch circuiting |  |  | 1000 | Branch circuiting |  |  | 1000 | Branch circuiting |  |  | 1000 | Branch circuiting |  |  | 1000 | Branch circuiting |  |  | 1000
| 2.3 | Fire Alarm
| a |  | Tenant provides fire alarm system, developer provides telephone line
|  |  | 2.3.a.1 |  | Assume landlord install 100' of telephone cabling in 1"RGS back to existing DACT for remote central station tie-in. Landlord to cover cost for testing base building fire alarm system after tenant system is installed. | 1000 |  |  | Assume landlord install 100' of telephone cabling in 1"RGS back to existing DACT for remote central station tie-in. Landlord to cover cost for testing base building fire alarm system after tenant system is installed. | 1000 |  |  | Assume landlord install 100' of telephone cabling in 1"RGS back to existing DACT for remote central station tie-in. Landlord to cover cost for testing base building fire alarm system after tenant system is installed. | 1000 |  |  | Assume landlord install 100' of telephone cabling in 1"RGS back to existing DACT for remote central station tie-in. Landlord to cover cost for testing base building fire alarm system after tenant system is installed. | 1000 |  |  | Assume landlord install 100' of telephone cabling in 1"RGS back to existing DACT for remote central station tie-in. Landlord to cover cost for testing base building fire alarm system after tenant system is installed. | 1000 |  |  | Assume landlord install 100' of telephone cabling in 1"RGS back to existing DACT for remote central station tie-in. Landlord to cover cost for testing base building fire alarm system after tenant system is installed. | 1000 |  |  | Assume landlord install 100' of telephone cabling in 1"RGS back to existing DACT for remote central station tie-in. Landlord to cover cost for testing base building fire alarm system after tenant system is installed. | 1000 |  |  | Assume landlord install 100' of telephone cabling in 1"RGS back to existing DACT for remote central station tie-in. Landlord to cover cost for testing base building fire alarm system after tenant system is installed. | 1000
|  |  | 2.3.a.2 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0
|  |  | 2.3.a.3 |  | Fire alarm system for tenant space. Tenant to install all initiating and notifcation devices in tenant space and provide a fire alarm panel in tenant space to connect all tenant initiating and notification devices. |  |  | 120000 | Fire alarm system for tenant space. Tenant to install all initiating and notifcation devices in tenant space and provide a fire alarm panel in tenant space to connect all tenant initiating and notification devices. |  |  | 120000 | Fire alarm system for tenant space. Tenant to install all initiating and notifcation devices in tenant space and provide a fire alarm panel in tenant space to connect all tenant initiating and notification devices. |  |  | 60000 | Fire alarm system for tenant space. Tenant to install all initiating and notifcation devices in tenant space and provide a fire alarm panel in tenant space to connect all tenant initiating and notification devices. |  |  | 41240 | Fire alarm system for tenant space. Tenant to install all initiating and notifcation devices in tenant space and provide a fire alarm panel in tenant space to connect all tenant initiating and notification devices. |  |  | 40000 | Fire alarm system for tenant space. Tenant to install all initiating and notifcation devices in tenant space and provide a fire alarm panel in tenant space to connect all tenant initiating and notification devices. |  |  | 40000 | Fire alarm system for tenant space. Tenant to install all initiating and notifcation devices in tenant space and provide a fire alarm panel in tenant space to connect all tenant initiating and notification devices. |  |  | 20000 | Fire alarm system for tenant space. Tenant to install all initiating and notifcation devices in tenant space and provide a fire alarm panel in tenant space to connect all tenant initiating and notification devices. |  |  | 20000
| b |  | When fire alarm system is required; developer provides a signaling line circuit from base building to retail space
|  |  | 2.3.b.1 |  | Assume landlord installs 100' of network work cabling in 1"RGS back to building fire alarm panel. Landlord to cover cost for testing base building fire alarm system after tenant system is installed. | 1000 |  |  | Assume landlord installs 100' of network work cabling in 1"RGS back to building fire alarm panel. Landlord to cover cost for testing base building fire alarm system after tenant system is installed. | 1000 |  |  | Assume landlord installs 100' of network work cabling in 1"RGS back to building fire alarm panel. Landlord to cover cost for testing base building fire alarm system after tenant system is installed. | 1000 |  |  | Assume landlord installs 100' of network work cabling in 1"RGS back to building fire alarm panel. Landlord to cover cost for testing base building fire alarm system after tenant system is installed. | 491 |  |  | Assume landlord installs 100' of network work cabling in 1"RGS back to building fire alarm panel. Landlord to cover cost for testing base building fire alarm system after tenant system is installed. | 1000 |  |  | Assume landlord installs 100' of network work cabling in 1"RGS back to building fire alarm panel. Landlord to cover cost for testing base building fire alarm system after tenant system is installed. | 1000 |  |  | Assume landlord installs 100' of network work cabling in 1"RGS back to building fire alarm panel. Landlord to cover cost for testing base building fire alarm system after tenant system is installed. | 1000 |  |  | Assume landlord installs 100' of network work cabling in 1"RGS back to building fire alarm panel. Landlord to cover cost for testing base building fire alarm system after tenant system is installed. | 1000
|  |  | 2.3.b.2 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0
|  |  | 2.3.b.3 |  | Fire alarm system for tenant space. Tenant to install all initiating and notofcation devices in tenant space and provide a fire alarm panel in tenant space to connect all tenant initiating and notification devices. |  |  | 120000 | Fire alarm system for tenant space. Tenant to install all initiating and notofcation devices in tenant space and provide a fire alarm panel in tenant space to connect all tenant initiating and notification devices. |  |  | 120000 | Fire alarm system for tenant space. Tenant to install all initiating and notofcation devices in tenant space and provide a fire alarm panel in tenant space to connect all tenant initiating and notification devices. |  |  | 60000 | Fire alarm system for tenant space. Tenant to install all initiating and notofcation devices in tenant space and provide a fire alarm panel in tenant space to connect all tenant initiating and notification devices. |  |  | 40000 | Fire alarm system for tenant space. Tenant to install all initiating and notofcation devices in tenant space and provide a fire alarm panel in tenant space to connect all tenant initiating and notification devices. |  |  | 40000 | Fire alarm system for tenant space. Tenant to install all initiating and notofcation devices in tenant space and provide a fire alarm panel in tenant space to connect all tenant initiating and notification devices. |  |  | 40000 | Fire alarm system for tenant space. Tenant to install all initiating and notofcation devices in tenant space and provide a fire alarm panel in tenant space to connect all tenant initiating and notification devices. |  |  | 20000 | Fire alarm system for tenant space. Tenant to install all initiating and notofcation devices in tenant space and provide a fire alarm panel in tenant space to connect all tenant initiating and notification devices. |  |  | 20000
| 3 | Plumbing
| 3.1 | Domestic Water
| a |  | Provide each retail space with a domestic water sub-meter with a valve and capped connection. Quantity of sub-meters is relative to building code |  | This is based on number of retail units. Assume 1 per each. Visual water meter inspection, or Building Management system monitors. Assume visual - Electronic metering of the master metering and they bill the owners. 1 water line for building, riser through building. Tap of riser with sub meter. Need to know how many connections / need to know how many retail units... make assumption based on a single instance of this item. Meter is fixed cost + Monitoring system |  |  |  | This is based on number of retail units. Assume 1 per each. Visual water meter inspection, or Building Management system monitors. Assume visual - Electronic metering of the master metering and they bill the owners. 1 water line for building, riser through building. Tap of riser with sub meter. Need to know how many connections / need to know how many retail units... make assumption based on a single instance of this item. Meter is fixed cost + Monitoring system |  |  |  | This is based on number of retail units. Assume 1 per each. Visual water meter inspection, or Building Management system monitors. Assume visual - Electronic metering of the master metering and they bill the owners. 1 water line for building, riser through building. Tap of riser with sub meter. Need to know how many connections / need to know how many retail units... make assumption based on a single instance of this item. Meter is fixed cost + Monitoring system |  |  |  | This is based on number of retail units. Assume 1 per each. Visual water meter inspection, or Building Management system monitors. Assume visual - Electronic metering of the master metering and they bill the owners. 1 water line for building, riser through building. Tap of riser with sub meter. Need to know how many connections / need to know how many retail units... make assumption based on a single instance of this item. Meter is fixed cost + Monitoring system |  |  |  | This is based on number of retail units. Assume 1 per each. Visual water meter inspection, or Building Management system monitors. Assume visual - Electronic metering of the master metering and they bill the owners. 1 water line for building, riser through building. Tap of riser with sub meter. Need to know how many connections / need to know how many retail units... make assumption based on a single instance of this item. Meter is fixed cost + Monitoring system |  |  |  | This is based on number of retail units. Assume 1 per each. Visual water meter inspection, or Building Management system monitors. Assume visual - Electronic metering of the master metering and they bill the owners. 1 water line for building, riser through building. Tap of riser with sub meter. Need to know how many connections / need to know how many retail units... make assumption based on a single instance of this item. Meter is fixed cost + Monitoring system
|  |  | 3.1.a.1 |  | Domestic water piping to unit, sub-meter, | 23500 |  |  | Domestic water piping to unit, sub-meter, | 23500 |  |  | Domestic water piping to unit, sub-meter, | 23500 |  |  | Domestic water piping to unit, sub-meter, | 23500 |  |  | Domestic water piping to unit, sub-meter, | 23500 |  |  | Domestic water piping to unit, sub-meter, | 23500 |  |  | Domestic water piping to unit, sub-meter, | 9500 |  |  | Domestic water piping to unit, sub-meter, | 23500
|  |  | 3.1.a.2 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0
|  |  | 3.1.a.3 |  | Water distribution (cold) |  |  | 36000 | Water distribution (cold) |  |  | 36000 | Water distribution (cold) |  |  | 36000 | Water distribution (cold) |  |  | 36000 | Water distribution (cold) |  |  | 36000 | Water distribution (cold) |  |  | 36000 | Water distribution (cold) |  |  | 12000 | Water distribution (cold) |  |  | 36000
| 3.2 | Hot Water
| a |  | Hot water system 1: Building provides hot water via tap into base building system
|  |  | 3.2.a.1 |  | Assume 750 CFH additional gas load to building hw system: piping to unit + sub-meter | 21700 |  |  |  | 21700 |  |  |  | 21700 |  |  |  | 21700 |  |  | Assume 750 CFH additional gas load to building hw system: piping to unit + sub-meter | 21700 |  |  |  | 0 |  |  |  | 0 |  |  | Assume 750 CFH additional gas load to building hw system: piping to unit + sub-meter | 21700
|  |  | 3.2.a.2 |  | N/A |  | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 |  | N/A |  | 0 |  |  |  | 0 |  |  |  | 0 |  | N/A |  | 0
|  |  | 3.2.a.3 |  | Water distribution (hot) |  |  | 36000 |  |  |  | 36000 |  |  | 36000 | 36000 |  |  |  | 36000 | Water distribution (hot) |  |  | 36000 |  |  |  | 0 |  |  |  | 0 | Water distribution (hot) |  |  | 36000
| b |  | Hot water system 2: Building provides Mechanical room with storage water heater for retail space
|  |  | 3.2.b.1 |  | Assume 750CFH gas load, piping to unit, sub-meter | 700 |  |  |  | 700 |  |  |  | 700 |  |  |  | 700 |  |  | Assume 750CFH gas load, piping to unit, sub-meter | 700 |  |  |  | 0 |  |  |  | 0 |  |  | Assume 750CFH gas load, piping to unit, sub-meter | 700
|  |  | 3.2.b.2 |  | 200 gallon storage tank |  | 5000 |  |  |  | 5000 |  |  |  | 5000 |  |  |  | 5000 |  | 200 gallon storage tank |  | 5000 |  |  |  | 0 |  |  |  | 0 |  | 200 gallon storage tank |  | 5000
|  |  | 3.2.b.3 |  | Water dist. |  |  | 36000 |  |  |  | 36000 |  |  |  | 36000 |  |  |  | 0 | Water dist. |  |  | 36000 | [7 empty] | 0 | Water dist. |  |  | 36000
| c |  | Hot water system 3: Provide instantaneous water heaters in restrooms or various applications, under 2gpm
|  |  | 3.2.c.1 |  | N/A | 0 | N/A |  | N/A | N/A | N/A | N/A | N/A | 0 |  | N/A | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0
|  |  | 3.2.c.2 |  | N/A | N/A | 0 |  | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0
|  |  | 3.2.c.3 |  | Instant water heaters (point of use) |  |  | 2000 | Instant water heaters (point of use) | Instant water heaters (point of use) | Instant water heaters (point of use) | 2000 | Instant water heaters (point of use) | Instant water heaters (point of use) | Instant water heaters (point of use) | 2000 | Instant water heaters (point of use) | Instant water heaters (point of use) | Instant water heaters (point of use) | 2000 | Instant water heaters (point of use) | Instant water heaters (point of use) | Instant water heaters (point of use) | 2000 | Instant water heaters (point of use) |  |  | 2000 | Instant water heaters (point of use) | Instant water heaters (point of use) | Instant water heaters (point of use) | 2000 | Instant water heaters (point of use) | Instant water heaters (point of use) | Instant water heaters (point of use) | 4000
| 3.3 | Sanitary Waste and Vent
| a |  | Dropped floor slab for flexibility of tenant sewer line
|  |  | 3.3.a.1 |  | Assume this will be located in kitchen areas. Landlord to provide pit and framing or in gym shower area for other retail types | 0 |  |  | Assume this will be located in kitchen areas. Landlord to provide pit and framing or in gym shower area for other retail types | 0 |  |  | Assume this will be located in kitchen areas. Landlord to provide pit and framing or in gym shower area for other retail types | 0 |  |  | Assume this will be located in kitchen areas. Landlord to provide pit and framing or in gym shower area for other retail types | 0 |  |  | Assume this will be located in kitchen areas. Landlord to provide pit and framing or in gym shower area for other retail types | 0 |  |  | Assume this will be located in kitchen areas. Landlord to provide pit and framing or in gym shower area for other retail types | 0 |  |  | Assume this will be located in kitchen areas. Landlord to provide pit and framing or in gym shower area for other retail types | 0 |  |  | Assume this will be located in kitchen areas. Landlord to provide pit and framing or in gym shower area for other retail types | 0
|  |  | 3.3.a.2 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0
|  |  | 3.3.a.3 |  | Floating level floor |  |  | 0 | Floating level floor |  |  | 0 | Floating level floor |  |  | 0 | Floating level floor |  |  | 0 | Floating level floor |  |  | 0 | Floating level floor |  |  | 0 | Floating level floor |  |  | 0 | Floating level floor |  |  | 0
| b |  | Provide capped waste pipe in a pre-set location for tenant to connect to and capped vent system connection
|  |  | 3.3.b.1 |  | 4" Waste and 2" Vent caps | 4040 |  |  | 4" Waste and 2" Vent caps | 4040 |  |  | 4" Waste and 2" Vent caps | 4040 |  |  | 4" Waste and 2" Vent caps | 4040 |  |  | 4" Waste and 2" Vent caps | 4040 |  |  | 4" Waste and 2" Vent caps | 4040 |  |  | 4" Waste and 2" Vent caps | 1260 |  |  | 4" Waste and 2" Vent caps | 4040
|  |  | 3.3.b.2 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0
|  |  | 3.3.b.3 |  | Waste and Vent connections |  |  | 1040 | Waste and Vent connections |  |  | 1040 | Waste and Vent connections |  |  | 1040 | Waste and Vent connections |  |  | 1040 | Waste and Vent connections |  |  | 1040 | Waste and Vent connections |  |  | 1040 | Waste and Vent connections |  |  | 260 | Waste and Vent connections |  |  | 1040
| c |  | Provide capped waste pipe in trench and capped vent system connection
|  |  | 3.3.c.1 |  | Trench, 4" Waste and 2" Vent caps | 4040 |  |  | Trench, 4" Waste and 2" Vent caps | 4040 |  |  | Trench, 4" Waste and 2" Vent caps | 4040 |  |  | Trench, 4" Waste and 2" Vent caps | 4040 |  |  | Trench, 4" Waste and 2" Vent caps | 4040 |  |  | Trench, 4" Waste and 2" Vent caps | 4040 |  |  | Trench, 4" Waste and 2" Vent caps | 1260 |  |  | Trench, 4" Waste and 2" Vent caps | 4040
|  |  | 3.3.c.2 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0
|  |  | 3.3.c.3 |  | Waste and Vent connections |  |  | 1040 | Waste and Vent connections |  |  | 1040 | Waste and Vent connections |  |  | 1040 | Waste and Vent connections |  |  | 1040 | Waste and Vent connections |  |  | 1040 | Waste and Vent connections |  |  | 1040 | Waste and Vent connections |  |  | 260 | Waste and Vent connections |  |  | 1040
| 3.4 | Grease Waste
| a |  | Provide centralized grease interceptor within sewer line
|  |  | 3.4.a.1 |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0
|  |  | 3.4.a.2 |  | tenant to provide interceptor based upon connected load of kitchen fixtures. If landlord provides, a 500 lb 250gpm allowance should be adequate. |  | 2500 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | tenant to provide interceptor based upon connected load of kitchen fixtures. If landlord provides, a 500 lb 250gpm allowance should be adequate. |  | 2500 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0
|  |  | 3.4.a.3 |  | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0
| b |  | Provide Interceptor
|  |  | 3.4.b.1 |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0
|  |  | 3.4.b.2 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0
|  |  | 3.4.b.3 |  | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0 | Equipped with an interceptor with a wire basket or similar device, removable for cleaning, that prevents passage into the drainage system of solids ½ inch or larger in size, string, rags, buttons or other materials detrimental to the public sewage system. |  |  | 50000
| 3.5 | Gas
| a |  | Capped and valved gas connection in retail space. | [34 empty] | Increases in connected loads are negligible compared to space heating loads.
|  |  | 3.5.a.1 |  | Assume 1000CFH connected load. Provide allowance for a gas booster, as ConEd only provides a guaranteed 4”w.c. and some appliances required 8” w.c. | 5000 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 | 0 |  | Assume 1000CFH connected load. Provide allowance for a gas booster, as ConEd only provides a guaranteed 4”w.c. and some appliances required 8” w.c. | 5000 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | Assume 3750CFH connected load. Provide allowance for a gas booster, as ConEd only provides a guaranteed 4”w.c. and some appliances required 8” w.c. | 5000
|  |  | 3.5.a.2 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0
|  |  | 3.5.a.3 |  | Gas piping within space |  |  | 11000 | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0 | Gas piping within space |  |  | 11000 | N/A |  |  | 0 | N/A |  |  | 0 | Gas piping within space |  |  | 11000
| b |  | Gas piping back to the meter room
|  |  | 3.5.b.1 |  | Assume landlord install 100' of 3" piping. | 11000 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | Assume landlord install 100' of 3" piping. | 11000 |  |  | N/A | 0 |  |  | N/A | 0 |  |  | Assume landlord install 100' of 3" piping. | 11000
|  |  | 3.5.b.2 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0
|  |  | 3.5.b.3 |  | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0
Fire Protection Systems
| 3.6 | Wet Sprinkler System
| a |  | Independent floor control assembly
|  |  | 3.6.a.1 |  | This is based on number of retail units. Assume 1 per each. There are two fire alarm connections per floor control assembly. Assume, landlord provides temporary sprinklers at 150SF per sprinkler (light hazard occupancy). Assume 3" floor control assembly. | 122600 |  |  | This is based on number of retail units. Assume 1 per each. There are two fire alarm connections per floor control assembly. Assume, landlord provides temporary sprinklers at 150SF per sprinkler (light hazard occupancy). Assume 3" floor control assembly. | 122600 |  |  | This is based on number of retail units. Assume 1 per each. There are two fire alarm connections per floor control assembly. Assume, landlord provides temporary sprinklers at 150SF per sprinkler (light hazard occupancy). Assume 3" floor control assembly. | 62600 |  |  | This is based on number of retail units. Assume 1 per each. There are two fire alarm connections per floor control assembly. Assume, landlord provides temporary sprinklers at 150SF per sprinkler (light hazard occupancy). Assume 3" floor control assembly. | 42600 |  |  | This is based on number of retail units. Assume 1 per each. There are two fire alarm connections per floor control assembly. Assume, landlord provides temporary sprinklers at 150SF per sprinkler (light hazard occupancy). Assume 3" floor control assembly. | 42600 |  |  | This is based on number of retail units. Assume 1 per each. There are two fire alarm connections per floor control assembly. Assume, landlord provides temporary sprinklers at 150SF per sprinkler (light hazard occupancy). Assume 3" floor control assembly. | 42600 |  |  | This is based on number of retail units. Assume 1 per each. There are two fire alarm connections per floor control assembly. Assume, landlord provides temporary sprinklers at 150SF per sprinkler (light hazard occupancy). Assume 3" floor control assembly. | 22600 |  |  | This is based on number of retail units. Assume 1 per each. There are two fire alarm connections per floor control assembly. Assume, landlord provides temporary sprinklers at 150SF per sprinkler (light hazard occupancy). Assume 3" floor control assembly. | 22600
|  |  | 3.6.a.2 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0 |  | N/A |  | 0
|  |  | 3.6.a.3 |  | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0 | N/A |  |  | 0
| 3.7 | Standpipe System
|  | a |  | Standpipe within retail space | This is based upon travel distances and partitions within spaces. Exact quantities cannot be determined. |  |  |  | This is based upon travel distances and partitions within spaces. Exact quantities cannot be determined. |  |  |  | This is based upon travel distances and partitions within spaces. Exact quantities cannot be determined. |  |  |  | This is based upon travel distances and partitions within spaces. Exact quantities cannot be determined. |  |  |  | This is based upon travel distances and partitions within spaces. Exact quantities cannot be determined. |  |  |  | This is based upon travel distances and partitions within spaces. Exact quantities cannot be determined. |  |  |  | This is based upon travel distances and partitions within spaces. Exact quantities cannot be determined. |  |  |  | This is based upon travel distances and partitions within spaces. Exact quantities cannot be determined.
I
II
III
| Subtotal Premium |  |  |  |  | 691580 | 420500 | #N/A |  | 619630 | 355000 | 738040 |  | 478170 | 319000 | 431020 |  | 416971 | 259000 | 280420 |  | 568230 | 254500 | 382530 |  | 327770 | 269340 | 244020 |  | 312070 | 231000 | 270320 |  | 333170 | 242000 | 345720
|  |  |  | HIGH |  | 1.5 | 1.5 | 1.5
|  |  |  | LOW |  | 0.75 | 0.75 | 0.75

## Supermarket
Tenant Use Type |  |  |  | Supermarket
Tenant ArEa (SF) |  |  |  | 12000
Building Height |  |  |  | 150
# bathrooms |  |  |  | 4
# units |  |  |  | 130
[5 empty] | NOTES | Quantity | Unit | Unit Cost | Total Cost | Total cost per Cost Alloc. | Total Cost per Option
| 1 | Mechanical
| 1.1 | Heating
| 1.1.a |  | 1.1.a.1 | 2" pipes at 20deg delta |  | 300 | LF | 80 | 24000 | 166500 | 214500
|  |  |  | Steel pipe 2" - 4" |  | 300 | LF | 130 | 39000
|  |  |  | Incremental Base Building Heat Source Increase by x MBH |  | 480 | MBH | 200 | 96000
|  |  |  | Meters: Flow & Temp |  | 3 | Ea | 2500 | 7500
|  |  | 1.1.a.2 | Electric unit heaters |  | 6 | Ea | 8000 | 48000 | 48000
|  |  | 1.1.a.3 | Included in AHU
| 1.1.b |  | 1.1.b.1 | Included in Cooling System | [6 empty] | 48000
|  |  | 1.1.b.2 | Electric unit heaters |  | 6 | Ea | 8000 | 48000 | 48000
|  |  | 1.1.b.3 | Included in AHU
| 1.1.c |  | 1.1.c.1 | 2" steam pipe |  | 300 | LF | 130 | 39000 | 58000 | 63000
|  |  |  | 2" condensate returns |  | 1 | Ea | 7500 | 7500
|  |  |  | Steam trap |  | 1 | Ea | 1000 | 1000
|  |  |  | 2 BMS points Meter Condensate Volume |  | 1 | LS | 2500 | 2500
|  |  |  | Steam fired unit heaters |  | 1 | Ea | 8000 | 8000
|  |  | 1.1.c.2 | 1" gas pipe |  | 100 | LF | 50 | 5000 | 5000
|  |  | 1.1.c.3 | N/A
| 1.1.d |  | 1.1.d.1 | 1 BMS point meter |  | 1 | Ea | 2500 | 2500 | 12500 | 108500
|  |  |  | Flue stainless steel exit roof |  | 1 | Ea | 10000 | 10000
|  |  |  | Shaft 18" x 18" (OD) |  | 150 | LF
|  |  | 1.1.d.2 | Boiler |  | 480 | MBH | 200 | 96000 | 96000
|  |  | 1.1.d.3 | Boiler |  | 0 | Ea | 200 | 0 | 0
| 1.2 | Cooling
| 1.2.a |  | 1.2.a.1 | 2 - 1/2" pipe at 14deg delta | Assumed 300 LF Copper | 300 | LF | 100 | 30000 | 100500 | 100500
|  |  |  | Steel pipe 4" - 6" |  | 300 | LF | 210 | 63000
|  |  |  | 3 BMS points Meters: Flow & Temp |  | 3 | Ea | 2500 | 7500
|  |  | 1.2.a.2 | N/A |  |  |  |  | 0 | 0
|  |  | 1.2.a.3 | Included in AHU |  |  |  |  | 0 | 0
| 1.2.b |  | 1.2.b.1 | 3" copper pipe | Assumed 300 LF Copper | 300 | LF | 120 | 36000 | 75000 | 75000
|  |  |  | Steel pipe 3" - 4" |  | 300 | LF | 130 | 39000
|  |  | 1.2.b.2 | N/A |  |  |  |  | 0 | 0
|  |  | 1.2.b.3 | Included in AHU |  |  |  |  | 0 | 0
| 1.2.c |  | 1.2.c.1 | Shaft for refrig. Pipe | Length = Height of Building | 150 | LF |  | 0 | 0 | 67500
|  |  | 1.2.c.2 | Roof Top Condenser Unit | Assumed Qty of 1 | 1 | Ea | 30000 | 30000 | 67500
|  |  |  | Refrigerant piping: 6" diameter Black Steel | Assumed 6" D | 150 | LF | 210 | 31500
|  |  |  | 1" copper pipe | Length = Height of Building | 150 | LF | 40 | 6000
|  |  | 1.2.c.3 | Included in AHU |  |  |  |  | 0 | 0
| 1.2.d |  | 1.2.d.1 | Shaft for refrig. Pipe | Length = Height of Building | 150 | LF |  | 0 | 0 | 67500
|  |  | 1.2.d.2 | Roof Top Condenser Unit | Assumed qty of 1 | 1 | Ea | 30000 | 30000 | 67500
|  |  |  | Refrigerant piping: 6" diameter Black Steel |  | 150 | LF | 210 | 31500
|  |  |  | 1" copper pipe | Length = Height of Building | 150 | LF | 40 | 6000
|  |  | 1.2.d.3 | Included in AHU |  |  |  |  | 0 | 0
| 1.2.e |  | 1.2.e.1 | N/A |  |  |  |  | 0 | 0 | 0
| 1.3 | Ventilation
| 1.3.a |  | 1.3.a.1 | 2.88 SF Louver | Assumed qty | 6 | Ea | 1000 | 6000 | 6000 | 66000
|  |  | 1.3.a.2 | Ducting from Louver to AHU |  | 300 | LF | 200 | 60000 | 60000
|  |  | 1.3.a.3 | AHU (Filters, mixing sections, heating coil, cooling coil, fan, return fan, duct work, grills) | Inclued in AHU line item |  |  |  | 0 | 0
| 1.4 | Air-Side Economizers
| 1.4.a |  | 1.4.a.1 | Included in AHU |  |  |  |  | 0 | 0 | 0
|  |  | 1.4.a.2 | Included in AHU |  |  |  |  | 0 | 0
|  |  | 1.4.a.3 | Included in AHU |  |  |  |  | 0 | 0
| 1.5 | Exhaust Air
| 1.5.a |  | 1.5.a.1 | Toilet exhaust fan |  | 1 | Ea | 5000 | 5000 | 6000 | 17000
|  |  |  | Louver - Toilet | 12" x 18" size assumption | 1 | Ea | 1000 | 1000
|  |  | 1.5.a.2 | Duct from Louver to fan | Assumed 30LF | 30 | LF | 200 | 6000 | 11000
|  |  |  | Toilet exhaust fan |  | 1 | Ea | 5000 | 5000
|  |  | 1.5.a.3 | N/A |  |  |  |  | 0 | 0
| 1.6 | Kitchen Exhaust
| 1.6.a |  | 1.6.a.1 | Provide shaft | [5 empty] | 1500 | 26500
|  |  |  | Louver - Kitchen | Assumed 2.88SF area Louver | 1 | Ea | 1500 | 1500
|  |  | 1.6.a.2 | Kitchen exhaust fan |  | 1 | Ea | 10000 | 10000 | 10000
|  |  | 1.6.a.3 | Exhaust hood |  | 1 | Ea | 15000 | 15000 | 15000
| 1.7 | Air-Handling Units
| 1.7.a |  | 1.7.a.1 | N/A |  |  |  |  | 0 | 0 | 57500
|  |  | 1.7.a.2 | N/A |  |  |  |  | 0 | 0
|  |  |  | AHU: Inside - Multizone - 15,600 CFM | Assumed this one is selected | 1 | Ea | 57500 | 57500 | 57500
|  |  |  | AHU: Inside - Single - 15,600 CFM |  |  | Ea | 53750 | 0
|  |  |  | AHU: Outside - Multizone - 15,600 CFM |  |  | Ea | 127500 | 0
|  |  |  | AHU: Outside - Single - 15,600 CFM |  |  | Ea | 127500 | 0
| 1.7.b |  | 1.7.b.1 | N/A |  |  |  |  | 0 | 0 | 57500
|  |  | 1.7.b.2 | N/A |  |  |  |  | 0 | 0
|  |  |  | AHU: Inside - Multizone - 15,600 CFM | Assumed this one is selected | 1 | Ea | 57500 | 57500 | 57500
|  |  |  | AHU: Inside - Single - 15,600 CFM |  |  | Ea | 53750 | 0
|  |  |  | AHU: Outside - Multizone - 15,600 CFM |  |  | Ea | 127500 | 0
|  |  |  | AHU: Outside - Single - 15,600 CFM |  |  | Ea | 127500 | 0
| 1.7.c |  | 1.7.c.1 | N/A |  |  |  |  | 0 | 0 | 57500
|  |  | 1.7.c.2 | N/A |  |  |  |  | 0 | 0
|  |  |  | AHU: Inside - Multizone - 15,600 CFM | Assumed this one is selected | 1 | Ea | 57500 | 57500 | 57500
|  |  |  | AHU: Inside - Single - 15,600 CFM |  |  | Ea | 53750 | 0
|  |  |  | AHU: Outside - Multizone - 15,600 CFM |  |  | Ea | 127500 | 0
|  |  |  | AHU: Outside - Single - 15,600 CFM |  |  | Ea | 127500 | 0
| 1.7.d |  | 1.7.d.1 | N/A |  |  |  |  | 0 | 0 | 57500
|  |  | 1.7.d.2 | N/A |  |  |  |  | 0 | 0
|  |  |  | AHU: Inside - Multizone - 15,600 CFM | Assumed this one is selected | 1 | Ea | 57500 | 57500 | 57500
|  |  |  | AHU: Inside - Single - 15,600 CFM |  |  | Ea | 53750 | 0
|  |  |  | AHU: Outside - Multizone - 15,600 CFM |  |  | Ea | 127500 | 0
|  |  |  | AHU: Outside - Single - 15,600 CFM |  |  | Ea | 127500 | 0
| 1.8 | Intakes and Exhaust
| 1.8.a |  | 1.8.a.1 | 2.88 SF Louver | Assumed qty | 6 | Ea | 1000 | 6000 | 6000 | 6000
|  |  | 1.8.a.2 | N/A
|  |  | 1.8.a.3 | N/A
| 1.8.b |  | 1.8.b.1 | Goose neck at Roof |  | 1 | Ea | 5000 | 5000 | 65000 | 65000
|  |  |  | Duct through shaft to unit | Assumed qty | 300 | LF | 200 | 60000
|  |  | 1.8.b.2 | N/A
|  |  | 1.8.b.3 | N/A
| 2 | Electrical
| 2.1 | Separate metering for electricity by utility
| 2.1.a |  | 2.1.a.1 | 800 amp - 208Y/120V three phase electrical service / cost covered by Con Edison | [5 empty] | 9550 | 10550
|  |  |  | CT Cabinet - 800A |  | 1 | Ea | 2550 | 2550
|  |  |  | Service Switch - 800A |  | 1 | Ea | 7000 | 7000
|  |  | 2.1.a.2 | N/A
|  |  | 2.1.a.3 | Branch circuiting |  | 100 | LF | 10 | 1000 | 1000
| 2.1.b |  | 2.1.b.1 | 2 sets of (4) 500mcm + (1)#1/0g in 3 1/2" c100' | Landlord will pay for it | 100 | LF | 160 | 16000 | 23700 | 24700
|  |  |  | Service Switch - 800A |  | 1 | Ea | 7000 | 7000
|  |  |  | Sub - meter |  | 1 | Ea | 700 | 700
|  |  | 2.1.b.2 | N/A
|  |  | 2.1.b.3 | Branch circuiting |  | 100 | LF | 10 | 1000 | 1000
| 2.2 | Emergency Power
| 2.2.a |  | 2.2.a.1 | N/A | [6 empty] | 1200
|  |  | 2.2.a.2 | N/A
|  |  | 2.2.a.3 | Emergency light fixtures (90 min battery pack) | Assumed qty | 8 | Ea | 150 | 1200 | 1200
| 2.2.b |  | 2.2.b.1 | N/A | [6 empty] | 26000
|  |  | 2.2.b.2 | N/A
|  |  | 2.2.b.3 | [6 empty] | 26000
|  |  |  | 15 KW natural gas generator + 60A 3pole disconnect switch |  | 1 | Ea | 26000 | 26000
| 2.2.c |  | 2.2.c.1 | [6 empty] | 28000 | 29000
|  |  |  | (4)#4 + (1)#8g in 1 1/4"c 100' |  | 100 | LF | 20 | 2000
|  |  |  | 15 KW natural gas generator + 60A 3pole disconnect switch |  | 1 | Ea | 26000 | 26000
|  |  | 2.2.c.2 | N/A
|  |  | 2.2.c.3 | Branch circuiting |  | 100 | LF | 10 | 1000 | 1000
| 2.3 | Fire Alarm
| 2.3.a |  | 2.3.a.1 | 100' telephone cabling in 1"RGS |  | 100 | LF | 10 | 1000 | 1000 | 121000
|  |  | 2.3.a.2 | N/A
|  |  | 2.3.a.3 | Fire alarm system (including notification devices & fire alarm panel) |  | 12000 | SF | 10 | 120000 | 120000
| 2.3.b |  | 2.3.b.1 | 100' telephone cabling in 1"RGS |  | 100 | LF | 10 | 1000 | 1000 | 121000
|  |  | 2.3.b.2 | N/A
|  |  | 2.3.b.3 | Fire alarm system (including notification devices & fire alarm panel) |  | 12000 | SF | 10 | 120000 | 120000
| 3 | Plumbing
| 3.1 | Domestic Water
| 3.1.a |  | 3.1.a.1 | Visual water meter inspection or BMS |  | 1 | Ea | 2500 | 2500 | 23500 | 59500
|  |  |  | Domestic water piping to unit - 3" Copper | Assumed qty. 3" diam | 300 | LF | 70 | 21000
|  |  | 3.1.a.2 | N/A
|  |  | 3.1.a.3 | Water distribution Cold - 3" Copper | Assumed qty. 3" diam | 300 | LF | 120 | 36000 | 36000
| 3.2 | Hot Water
| 3.2.a |  | 3.2.a.1 | [6 empty] | 21700 | 57700
|  |  |  | Domestic water piping to unit - 3" Copper | Assumed qty. 3" diam | 300 | LF | 70 | 21000
|  |  |  | Sub - meter |  | 1 | Ea | 700 | 700
|  |  | 3.2.a.2 | N/A
|  |  | 3.2.a.3 | Water distribution Hot - 3" Copper | Assumed qty. 3" diam | 300 | LF | 120 | 36000 | 36000
| 3.2.b |  | 3.2.b.1 | [6 empty] | 700 | 41700
|  |  |  | Sub - meter |  | 1 | Ea | 700 | 700
|  |  | 3.2.b.2 | Storage tank (200 gallons) | Assumed 200 gallons | 1 | Ea | 5000 | 5000 | 5000
|  |  | 3.2.b.3 | Water distribution Hot - 3" Copper | Assumed qty. 3" diam | 300 | LF | 120 | 36000 | 36000
| 3.2.c |  | 3.2.c.1 | N/A | [6 empty] | 2000
|  |  | 3.2.c.2 | N/A
|  |  | 3.2.c.3 | Instant water heaters | Assumed qty | 1 | Ea | 2000 | 2000 | 2000
| 3.3 | Sanitary Waste and Vent
| 3.3.a |  | 3.3.a.1 | Dropped floor slab (kitchen areas) |  |  |  |  | 0 | 0 | 0
|  |  |  | Pit |  |  |  |  | 0
|  |  |  | Framing |  |  |  |  | 0
|  |  | 3.3.a.2 | N/A
|  |  | 3.3.a.3 | Floating level floor |  |  |  |  | 0 | 0
| 3.3.b |  | 3.3.b.1 | 4" PVC capped waste pipe | Assumed PVC | 300 | LF | 10 | 3000 | 4040 | 5080
|  |  |  | 2" cap vent | Assumed qty | 8 | Ea | 130 | 1040
|  |  | 3.3.b.2 | N/A
|  |  | 3.3.b.3 | 2" cap vent | Assumed qty | 8 | Ea | 130 | 1040 | 1040
| 3.3.c |  | 3.3.c.1 | [6 empty] | 4040 | 5080
|  |  |  | 4" PVC capped waste pipe | Assumed PVC | 300 | LF | 10 | 3000
|  |  |  | 2" cap vent | Assumed qty | 8 | Ea | 130 | 1040
|  |  | 3.3.c.2 | N/A
|  |  | 3.3.c.3 | 2" cap vent | Assumed qty | 8 | Ea | 130 | 1040 | 1040
| 3.4 | Grease Waste
| 3.4.a |  | 3.4.a.1 | N/A | [6 empty] | 2500
|  |  | 3.4.a.2 | Grease interceptor |  | 1 | Ea | 2500 | 2500 | 2500
|  |  | 3.4.a.3 | N/A
| 3.4.b |  | 3.4.b.1 | N/A | [6 empty] | 0
|  |  | 3.4.b.2 | N/A
|  |  | 3.4.b.3 | N/A
| 3.5 | Gas
| 3.5.a |  | 3.5.a.1 | Gas booster |  | 1 | Ea | 5000 | 5000 | 5000 | 16000
|  |  | 3.5.a.2 | N/A
|  |  | 3.5.a.3 | 3" gas pipe |  | 100 | LF | 110 | 11000 | 11000
| 3.5.b |  | 3.5.b.1 | 3" gas pipe |  | 100 | LF | 110 | 11000 | 11000 | 11000
|  |  | 3.5.b.2 | N/A
|  |  | 3.5.b.3 | N/A
Fire Protection Systems
| 3.6 | Wet Sprinkler System
| 3.6.a |  | 3.6.a.1 | Sprinklers |  | 12000 | SF | 10 | 120000 | 122600 | 122600
|  |  |  | 3" floor control assembly |  | 1 | EA | 2600 | 2600
|  |  | 3.6.a.2 | N/A
|  |  | 3.6.a.3 | N/A
| 3.7 | Standpipe System

## PharmacyL
Tenant Use Type |  |  |  | Pharmacy (Large)
Tenant Area (SF) |  |  |  | 12000
Building Height |  |  |  | 150
# bathrooms |  |  |  | 3
# units |  |  |  | 130
[5 empty] | NOTES | Quantity | Unit | Unit Cost | Total Cost | Total cost per Cost Alloc. | Total Cost per Option
| 1 | Mechanical
| 1.1 | Heating
| 1.1.a |  | 1.1.a.1 | 2" pipes at 20deg delta |  | 300 | LF | 80 | 24000 | 166500 | 214500
|  |  |  | Steel pipe 2" - 4" |  | 300 | LF | 130 | 39000
|  |  |  | Incremental Base Building Heat Source Increase by x MBH |  | 480 | MBH | 200 | 96000
|  |  |  | Meters: Flow & Temp |  | 3 | Ea | 2500 | 7500
|  |  | 1.1.a.2 | Electric unit heaters |  | 6 | Ea | 8000 | 48000 | 48000
|  |  | 1.1.a.3 | Included in AHU
| 1.1.b |  | 1.1.b.1 | Included in Cooling System | [6 empty] | 0
|  |  | 1.1.b.2 | N/A
|  |  | 1.1.b.3 | N/A
| 1.1.c |  | 1.1.c.1 | N/A | [6 empty] | 0
|  |  | 1.1.c.2 | N/A
|  |  | 1.1.c.3 | N/A
| 1.1.d |  | 1.1.d.1 | 1 bms point meter |  | 1 | Ea | 2500 | 2500 | 12500 | 108500
|  |  |  | Flue stainless steel exit roof |  | 1 | Ea | 10000 | 10000
|  |  |  | Shaft 18" x 18" (OD) |  | 150 | LF
|  |  | 1.1.d.2 | Boiler |  | 480 | MBH | 200 | 96000 | 96000
|  |  | 1.1.d.3 | Boiler |  | 0 | MBH | 200 | 0 | 0
| 1.2 | Cooling
| 1.2.a |  | 1.2.a.1 | 3" pipe at 14deg delta |  | 300 | LF | 120 | 36000 | 106500 | 106500
|  |  |  | Steel pipe 4" - 6" |  | 300 | LF | 210 | 63000
|  |  |  | 3 BMS points Meters: Flow & Temp |  | 3 | Ea | 2500 | 7500
|  |  | 1.2.a.2 | N/A
|  |  | 1.2.a.3 | Included in AHU
| 1.2.b |  | 1.2.b.1 | 4" Copper pipe |  | 300 | LF | 190 | 57000 | 96000 | 96000
|  |  |  | Steel pipe 3" - 4" |  | 300 | LF | 130 | 39000
|  |  | 1.2.b.2 | N/A
|  |  | 1.2.b.3 | Included in AHU
| 1.2.c |  | 1.2.c.1 | Shaft for refrig. Pipe |  | 150 | LF | 0 | 0 | 0 | 67500
|  |  | 1.2.c.2 | Roof Top Condenser Unit |  | 1 | Ea | 30000 | 30000 | 67500
|  |  |  | Refrigerant piping: 6" diameter Black Steel |  | 150 | LF | 210 | 31500
|  |  |  | 1" copper pipe |  | 150 | LF | 40 | 6000
|  |  | 1.2.c.3 | Included in AHU |  |  |  |  | 0 | 0
| 1.2.d |  | 1.2.d.1 | Shaft for refrig. Pipe |  | 150 | LF | 0 | 0 | 0 | 67500
|  |  | 1.2.d.2 | Roof Top Condenser Unit |  | 1 | Ea | 30000 | 30000 | 67500
|  |  |  | Refrigerant piping: 6" diameter Black Steel |  | 150 | LF | 210 | 31500
|  |  |  | 1" copper pipe |  | 150 | LF | 40 | 6000
|  |  | 1.2.d.3 | Included in AHU
| 1.2.e |  | 1.2.e.1 | N/A | [6 empty] | 0
| 1.3 | Ventilation
| 1.3.a |  | 1.3.a.1 | 5.52 SF Louver |  | 6 | Ea | 1500 | 9000 | 9000 | 69000
|  |  | 1.3.a.2 | Ducting from Louver to AHU |  | 300 | LF | 200 | 60000 | 60000
|  |  | 1.3.a.3 | AHU (Filters, mixing sections, heating coil, cooling coil, fan, return fan, duct work, grills) | Included in AHU line item | 0 | 0 | 0 | 0 | 0
| 1.4 | Air-Side Economizers
| 1.4.a |  | 1.4.a.1 | Included in AHU | [6 empty] | 0
|  |  | 1.4.1.2 | Included in AHU
|  |  | 1.4.a.3 | Included in AHU
| 1.5 | Exhaust Air
| 1.5.a |  | 1.5.a.1 | Toilet exhaust fan |  | 1 | Ea | 5000 | 5000 | 6000 | 17000
|  |  |  | 2.88 SF Louver |  | 1 | Ea | 1000 | 1000
|  |  |  | Tenant & public restrooms |  |  |  |  | 0
|  |  | 1.5.a.2 | Duct from Louver to fan |  | 30 | LF | 200 | 6000 | 11000
|  |  |  | Toilet exhaust fan |  | 1 | Ea | 5000 | 5000
1.5.a.3
| 1.6 | Kitchen Exhaust
| 1.6.a |  | 1.6.a.1 | N/A | [6 empty] | 0
|  |  | 1.6.a.2 | N/A
|  |  | 1.6.a.3 | N/A
| 1.7 | Air-Handling Units
| 1.7.a |  | 1.7.a.1 | N/A | [6 empty] | 90190
|  |  | 1.7.a.2 | N/A
|  |  | 1.7.a.3 | 2CFM / SF | 24000 |  |  |  | 0 | 90190
|  |  |  | AHU: Inside - Multizone - 24,000 CFM | Assumed this one is selected | 1 | Ea | 90190 | 90190
|  |  |  | AHU: Inside - Single - 24,000 CFM |  | 0 | Ea | 73750 | 0
|  |  |  | AHU: Outside - Multizone - 24,000 CFM |  | 0 | Ea | 221250 | 0
|  |  |  | AHU: Outside - Single - 24,000 CFM |  | 0 | Ea | 221250 | 0
| 1.7.b |  | 1.7.b.1 | N/A | [6 empty] | 90190
|  |  | 1.7.b.2 | N/A
|  |  | 1.7.b.3 | 2CFM / SF | 24000 |  |  |  | 0 | 90190
|  |  |  | AHU: Inside - Multizone - 24,000 CFM | Assumed this one is selected | 1 | Ea | 90190 | 90190
|  |  |  | AHU: Inside - Single - 24,000 CFM |  | 0 | Ea | 73750 | 0
|  |  |  | AHU: Outside - Multizone - 24,000 CFM |  | 0 | Ea | 221250 | 0
|  |  |  | AHU: Outside - Single - 24,000 CFM |  | 0 | Ea | 221250 | 0
| 1.7.c |  | 1.7.c.1 | N/A | [6 empty] | 90190
|  |  | 1.7.c.2 | N/A
|  |  | 1.7.c.3 | 2CFM / SF | 24000 |  |  |  | 0 | 90190
|  |  |  | AHU: Inside - Multizone - 24,000 CFM | Assumed this one is selected | 1 | Ea | 90190 | 90190
|  |  |  | AHU: Inside - Single - 24,000 CFM |  | 0 | Ea | 73750 | 0
|  |  |  | AHU: Outside - Multizone - 24,000 CFM |  | 0 | Ea | 221250 | 0
|  |  |  | AHU: Outside - Single - 24,000 CFM |  | 0 | Ea | 221250 | 0
| 1.7.d |  | 1.7.d.1 | N/A | [6 empty] | 90190
|  |  | 1.7.d.2 | N/A
|  |  | 1.7.d.3 | 2CFM / SF | 24000 |  |  |  | 0 | 90190
|  |  |  | AHU: Inside - Multizone - 24,000 CFM | Assumed this one is selected | 1 | Ea | 90190 | 90190
|  |  |  | AHU: Inside - Single - 24,000 CFM |  | 0 | Ea | 73750 | 0
|  |  |  | AHU: Outside - Multizone - 24,000 CFM |  | 0 | Ea | 221250 | 0
|  |  |  | AHU: Outside - Single - 24,000 CFM |  | 0 | Ea | 221250 | 0
| 1.8 | Intakes and Exhaust
| 1.8.a |  | 1.8.a.1 | 5.52 SF Louver |  | 6 | Ea | 1500 | 9000 | 9000 | 9000
|  |  | 1.8.a.2 | N/A
|  |  | 1.8.a.3 | N/A
| 1.8.b |  | 1.8.b.1 | Goose neck at Roof |  | 1 | Ea | 5000 | 5000 | 65000 | 65000
|  |  |  | Duct through shaft to unit |  | 300 | LF | 200 | 60000
|  |  | 1.8.b.2 | N/A
|  |  | 1.8.b.3 | [5 empty] | 0 | 0
| 2 | Electrical
| 2.1 | Separate metering for electricity by utility
| 2.1.a |  | 2.1.a.1 | 400 amp - 208Y/120V three phase electrical service / cost covered by Con Edison | [5 empty] | 6850 | 7850
|  |  |  | CT Cabinet - 400A |  | 1 | Ea | 1850 | 1850
|  |  |  | Service Switch - 400A |  | 1 | Ea | 5000 | 5000
|  |  | 2.1.a.2 | N/A
|  |  | 2.1.a.3 | Branch circuiting |  | 100 | LF | 10 | 1000 | 1000
| 2.1.b |  | 2.1.b.1 | 1 set of 4 500mcm + (1)#1/0g in 3 1/2" c100' | Landlord will pay for it | 100 | LF | 90 | 9000 | 14700 | 15700
|  |  |  | Service Switch - 400A |  | 1 | Ea | 5000 | 5000
|  |  |  | Sub - meter |  | 1 | Ea | 700 | 700
|  |  | 2.1.b.2 | N/A
|  |  | 2.1.b.3 | Branch circuiting |  | 100 | LF | 10 | 1000 | 1000
| 2.2 | Emergency Power
| 2.2.a |  | 2.2.a.1 | N/A | [6 empty] | 1200
|  |  | 2.2.a.2 | N/A
|  |  | 2.2.a.3 | Emergency light fixtures (90 min battery pack) |  | 8 | Ea | 150 | 1200 | 1200
N/A
| 2.2.b |  | 2.2.b.1 | N/A | [6 empty] | 21000
|  |  | 2.2.b.2 | N/A
|  |  | 2.2.b.3 | [5 empty] | 0 | 21000
|  |  |  | 10 KW natural gas generator + 30A 3pole disconnect switch |  | 1 | Ea | 21000 | 21000
| 2.2.c |  | 2.2.c.1 | 10Kw worth of emergency power | [5 empty] | 23000 | 24000
|  |  |  | (4)#10 + (1)#12g in 1"c 100' |  | 100 | LF | 20 | 2000
|  |  |  | 10 KW natural gas generator + 30A 3pole disconnect switch |  | 1 | Ea | 21000 | 21000
|  |  | 2.2.c.2 | N/A
|  |  | 2.2.c.3 | Branch circuiting |  | 100 | LF | 10 | 1000 | 1000
| 2.3 | Fire Alarm
| 2.3.a |  | 2.3.a.1 | 100' telephone cabling in 1"RGS |  | 100 | LF | 10 | 1000 | 1000 | 121000
|  |  | 2.3.a.2 | N/A
|  |  | 2.3.a.3 | Fire alarm system (including notification devices & fire alarm panel) |  | 12000 | SF | 10 | 120000 | 120000
| 2.3.b |  | 2.3.b.1 | 100' telephone cabling in 1"RGS |  | 100 | LF | 10 | 1000 | 1000 | 121000
|  |  | 2.3.b.2 | N/A
|  |  | 2.3.b.3 | Fire alarm system (including notification devices & fire alarm panel) |  | 12000 | SF | 10 | 120000 | 120000
| 3 | Plumbing
| 3.1 | Domestic Water
| 3.1.a |  | 3.1.a.1 | Visual water meter inspection or BMS |  | 1 | Ea | 2500 | 2500 | 23500 | 59500
|  |  |  | Domestic water piping to unit - 3" Copper |  | 300 | LF | 70 | 21000
|  |  | 3.1.a.2 | N/A
|  |  | 3.1.a.3 | Water distribution Cold - 3" Copper |  | 300 | LF | 120 | 36000 | 36000
| 3.2 | Hot Water
| 3.2.a |  | 3.2.a.1 | 750CFH to load additionally to building HW system |  |  |  | 0 | 0 | 21700 | 57700
|  |  |  | Domestic water piping to unit - 3" Copper |  | 300 | LF | 70 | 21000
|  |  |  | Sub - meter |  | 1 | Ea | 700 | 700
|  |  | 3.2.a.2 | N/A
|  |  | 3.2.a.3 | Water distribution Hot - 3" Copper |  | 300 | LF | 120 | 36000 | 36000
| 3.2.b |  | 3.2.b.1 | 750CFH to load additionally to building HW system |  |  |  | 0 | 0 | 700 | 41700
|  |  |  | Sub - meter |  | 1 | Ea | 700 | 700
|  |  | 3.2.b.2 | Storage tank (200 gallons) |  | 1 | Ea | 5000 | 5000 | 5000
|  |  | 3.2.b.3 | Water distribution Hot - 3" Copper |  | 300 | LF | 120 | 36000 | 36000
| 3.2.c |  | 3.2.c.1 | N/A | [6 empty] | 2000
|  |  | 3.2.c.2 | N/A |  | 1 | EA
|  |  | 3.2.c.3 | Instant water heaters |  | 1 | EA | 2000 | 2000 | 2000
| 3.3 | Sanitary Waste and Vent
| 3.3.a |  | 3.3.a.1 | Dropped floor slab (kitchen areas) |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Pit |  | 0 | 0 | 0 | 0
|  |  |  | Framing |  | 0 | 0 | 0 | 0
|  |  | 3.3.a.2 | N/A
|  |  | 3.3.a.3 | Floating level floor |  | 0 | 0 | 0 | 0 | 0
| 3.3.b |  | 3.3.b.1 | 4" PVC capped waste pipe |  | 300 | LF | 10 | 3000 | 4040 | 5080
|  |  |  | 2" cap vent |  | 8 | EA | 130 | 1040
|  |  | 3.3.b.2 | N/A
|  |  | 3.3.b.3 | 2" cap vent |  | 8 | Ea | 130 | 1040 | 1040
| 3.3.c |  | 3.3.c.1 | Trench | [5 empty] | 4040 | 5080
|  |  |  | 4" PVC capped waste pipe |  | 300 | LF | 10 | 3000
|  |  |  | 2" cap vent |  | 8 | EA | 130 | 1040
|  |  | 3.3.c.2 | N/A
|  |  | 3.3.c.3 | 2" cap vent |  | 8 | Ea | 130 | 1040 | 1040
| 3.4 | Grease Waste
| 3.4.a |  | 3.4.a.1 | N/A | [6 empty] | 0
|  |  | 3.4.a.2 | N/A
|  |  | 3.4.a.3 | N/A
| 3.4.b |  | 3.4.b.1 | N/A | [6 empty] | 0
|  |  | 3.4.b.2 | N/A
|  |  | 3.4.b.3 | N/A
| 3.5 | Gas
| 3.5.a |  | 3.5.a.1 | N/A | [6 empty] | 0
|  |  | 3.5.a.2 | N/A
|  |  | 3.5.a.3 | N/A
| 3.5.b |  | 3.5.b.1 | N/A | [6 empty] | 0
|  |  | 3.5.b.2 | N/A
|  |  | 3.5.b.3 | N/A
Fire Protection Systems
| 3.6 | Wet Sprinkler System
| 3.6.a |  | 3.6.a.1 | Sprinklers |  | 12000 | SF | 10 | 120000 | 122600 | 122600
|  |  |  | 3" floor control assembly |  | 1 | Ea | 2600 | 2600
|  |  | 3.6.a.2 | N/A
|  |  | 3.6.a.3 | N/A
| 3.7 | Standpipe System

## PharmacyS
Tenant Use Type |  |  |  | Pharmacy (Small)
Tenant Area (SF) |  |  |  | 6000
Building Height |  |  |  | 150
# bathrooms |  |  |  | 2
# units |  |  |  | 130
[5 empty] | Notes | Quantity | Unit | Unit Cost | Total Cost | Total cost per Cost Alloc. | Total Cost per Option
| 1 | Mechanical
| 1.1 | Heating
| 1.1.a |  | 1.1.a.1 | 1 - 1/2" pipes at 20deg delta |  | 100 | LF | 60 | 6000 | 68500 | 92500
|  |  |  | Steel pipe 1" - 2" |  | 100 | LF | 70 | 7000
|  |  |  | Incremental Base Building Heat Source Increase by x MBH |  | 240 | MBH | 200 | 48000
|  |  |  | Meters: Flow & Temp |  | 3 | Ea | 2500 | 7500
|  |  | 1.1.a.2 | Electric unit heaters |  | 3 | Ea | 8000 | 24000 | 24000
|  |  | 1.1.a.3 | Included in AHU
| 1.1.b |  | 1.1.b.1 | Included in Cooling System | [6 empty] | 0
|  |  | 1.1.b.2 | N/A
|  |  | 1.1.b.3 | N/A
| 1.1.c |  | 1.1.c.1 | N/A | [6 empty] | 0
|  |  | 1.1.c.2 | N/A
|  |  | 1.1.c.3 | N/A
| 1.1.d |  | 1.1.d.1 | 1 bms point meter |  | 1 | Ea | 2500 | 2500 | 12500 | 60500
|  |  |  | Flue stainless steel exit roof |  | 1 | Ea | 10000 | 10000
|  |  |  | Shaft 18" x 18" (OD) |  |  | LF | 0 | 0
|  |  | 1.1.d.2 | Boiler |  | 240 | MBH | 200 | 48000 | 48000
|  |  | 1.1.d.3 | Boiler |  | 0 | MBH | 200 | 0 | 0
| 1.2 | Cooling
| 1.2.a |  | 1.2.a.1 | 2 - 1/2" pipe at 14deg delta |  | 300 | LF | 100 | 30000 | 100500 | 100500
|  |  |  | Steel pipe 4" - 6" |  | 300 | LF | 210 | 63000
|  |  |  | 3 BMS points Meters: Flow & Temp |  | 3 | Ea | 2500 | 7500
|  |  | 1.2.a.2 | N/A
|  |  | 1.2.a.3 | Included in AHU
| 1.2.b |  | 1.2.b.1 | 3" copper pipe |  | 300 | LF | 120 | 36000 | 75000 | 75000
|  |  |  | Steel pipe 3" - 4" |  | 300 | LF | 130 | 39000
|  |  | 1.2.b.2 | N/A
|  |  | 1.2.b.3 | Included in AHU
| 1.2.c |  | 1.2.c.1 | Shaft for refrig. Pipe |  | 150 | LF | 0 | 0 | 0 | 67500
|  |  | 1.2.c.2 | Roof Top Condenser unit |  | 1 | Ea | 30000 | 30000 | 67500
|  |  |  | Refrigerant piping: 6" diameter Black Steel |  | 150 | LF | 210 | 31500
|  |  |  | 1" copper pipe |  | 150 | LF | 40 | 6000
|  |  | 1.2.c.3 | Included in AHU
| 1.2.d |  | 1.2.d.1 | Shaft for refrig. Pipe |  | 150 | LF | 0 | 0 | 0 | 67500
|  |  | 1.2.d.2 | Roof Top Condenser unit |  | 1 | Ea | 30000 | 30000 | 67500
|  |  |  | Refrigerant piping: 6" diameter Black Steel |  | 150 | LF | 210 | 31500
|  |  |  | 1" copper pipe |  | 150 | LF | 40 | 6000
|  |  | 1.2.d.3 | Included in AHU
| 1.2.e |  | 1.2.e.1 | N/A | [6 empty] | 0
| 1.3 | Ventilation
| 1.3.a |  | 1.3.a.1 | 2.88 SF Louver |  | 4 | Ea | 1000 | 4000 | 4000 | 64000
|  |  | 1.3.a.2 | Ducting from Louver to AHU |  | 300 | LF | 200 | 60000 | 60000
|  |  | 1.3.a.3 | AHU (Filters, mixing sections, heating coil, cooling coil, fan, return fan, duct work, grills) | Included in AHU line item | 1 | Ea | 0 | 0
| 1.4 | Air-Side Economizers
| 1.4.a |  | 1.4.a.1 | Included in AHU | [6 empty] | 0
|  |  | 1.4.1.2 | Included in AHU
|  |  | 1.4.a.3 | Included in AHU
| 1.5 | Exhaust Air
| 1.5.a |  | 1.5.a.1 | Toilet exhaust fan |  | 1 | Ea | 5000 | 5000 | 6000 | 17000
|  |  |  | 2.88 SF Louver |  | 1 | Ea | 1000 | 1000
Tenant & public restrooms
|  |  | 1.5.a.2 | Duct from Louver to fan |  | 30 | LF | 200 | 6000 | 11000
|  |  |  | Toilet exhaust fan |  | 1 | Ea | 5000 | 5000
1.5.a.3
| 1.6 | Kitchen Exhaust
| 1.6.a |  | 1.6.a.1 | N/A | [6 empty] | 0
|  |  | 1.6.a.2 | N/A
|  |  | 1.6.a.3 | N/A
| 1.7 | Air-Handling Units
| 1.7.a |  | 1.7.a.1 | N/A | [6 empty] | 46250
|  |  | 1.7.a.2 | N/A
|  |  | 1.7.a.3 | 2CFM / SF | 12000 |  |  |  |  | 46250
|  |  |  | AHU: Inside - Multizone - 12,000 CFM | Assumed this one is selected | 1 | Ea | 46250 | 46250
|  |  |  | AHU: Inside - Single - 12,000 CFM |  |  | Ea | 40000 | 0
|  |  |  | AHU: Outside - Multizone - 12,000 CFM |  |  | Ea | 127500 | 0
|  |  |  | AHU: Outside - Single - 12,000 CFM |  |  | Ea | 127500 | 0
| 1.7.b |  | 1.7.b.1 | N/A | [6 empty] | 46250
|  |  | 1.7.b.2 | N/A
|  |  | 1.7.b.3 | 2CFM / SF | 12000 |  |  |  |  | 46250
|  |  |  | AHU: Inside - Multizone - 12,000 CFM | Assumed this one is selected | 1 | Ea | 46250 | 46250
|  |  |  | AHU: Inside - Single - 12,000 CFM |  |  | Ea | 40000 | 0
|  |  |  | AHU: Outside - Multizone - 12,000 CFM |  |  | Ea | 127500 | 0
|  |  |  | AHU: Outside - Single - 12,000 CFM |  |  | Ea | 127500 | 0
| 1.7.c |  | 1.7.c.1 | N/A | [6 empty] | 46250
|  |  | 1.7.c.2 | N/A
|  |  | 1.7.c.3 | 2CFM / SF | 12000 |  |  |  |  | 46250
|  |  |  | AHU: Inside - Multizone - 12,000 CFM | Assumed this one is selected | 1 | Ea | 46250 | 46250
|  |  |  | AHU: Inside - Single - 12,000 CFM |  |  | Ea | 40000 | 0
|  |  |  | AHU: Outside - Multizone - 12,000 CFM |  |  | Ea | 127500 | 0
|  |  |  | AHU: Outside - Single - 12,000 CFM |  |  | Ea | 127500 | 0
| 1.7.d |  | 1.7.d.1 | N/A | [6 empty] | 46250
|  |  | 1.7.d.2 | N/A
|  |  | 1.7.d.3 | 2CFM / SF | 12000 |  |  |  |  | 46250
|  |  |  | AHU: Inside - Multizone - 12,000 CFM | Assumed this one is selected | 1 | Ea | 46250 | 46250
|  |  |  | AHU: Inside - Single - 12,000 CFM |  |  | Ea | 40000 | 0
|  |  |  | AHU: Outside - Multizone - 12,000 CFM |  |  | Ea | 127500 | 0
|  |  |  | AHU: Outside - Single - 12,000 CFM |  |  | Ea | 127500 | 0
| 1.8 | Intakes and Exhaust
| 1.8.a |  | 1.8.a.1 | 2.88 SF Louver |  | 4 | Ea | 1000 | 4000 | 4000 | 4000
|  |  | 1.8.a.2 | N/A
|  |  | 1.8.a.3 | N/A
| 1.8.b |  | 1.8.b.1 | Goose neck at Roof |  | 1 | Ea | 5000 | 5000 | 65000 | 65000
|  |  |  | Duct through shaft to unit |  | 300 | LF | 200 | 60000
|  |  | 1.8.b.2 | N/A
1.8.b.3
| 2 | Electrical
| 2.1 | Separate metering for electricity by utility
| 2.1.a |  | 2.1.a.1 | 200 amp - 208Y/120V three phase electrical service / cost covered by Con Edison | [5 empty] | 3300 | 4300
|  |  |  | CT Cabinet - 200A |  | 1 | Ea | 1550 | 1550
|  |  |  | Service Switch - 200A |  | 1 | Ea | 1750 | 1750
|  |  | 2.1.a.2 | N/A
|  |  | 2.1.a.3 | Branch circuiting |  | 100 | LF | 10 | 1000 | 1000
| 2.1.b |  | 2.1.b.1 | 1 sets of (4) 3/0 + (1)#2g in 2 1/2"c 100' | Landlord will pay for it | 100 | LF | 50 | 5000 | 7450 | 8450
|  |  |  | Service Switch - 200A |  | 1 | Ea | 1750 | 1750
|  |  |  | Sub - meter |  | 1 | Ea | 700 | 700
|  |  | 2.1.b.2 | N/A
|  |  | 2.1.b.3 | Branch circuiting |  | 100 | LF | 10 | 1000 | 1000
| 2.2 | Emergency Power
| 2.2.a |  | 2.2.a.1 | N/A | [6 empty] | 600
|  |  | 2.2.a.2 | N/A
|  |  | 2.2.a.3 | Emergency light fixtures (90 min battery pack) | Assumed qty | 4 | Ea | 150 | 600 | 600
| 2.2.b |  | 2.2.b.1 | N/A | [6 empty] | 10340
|  |  | 2.2.b.2 | N/A
|  |  | 2.2.b.3 | [6 empty] | 10340
|  |  |  | 5 KW gas generator with 15A 3pole disconnect switch |  | 1 | Ea | 10340 | 10340
| 2.2.c |  | 2.2.c.1 | [6 empty] | 13340 | 14340
|  |  |  | (4)#10 + (1)#2g in 1"c 100' |  | 100 | LF | 30 | 3000
|  |  |  | 5 KW gas generator with 15A 3pole disconnect switch |  | 1 | Ea | 10340 | 10340
|  |  | 2.2.c.2 | N/A
|  |  | 2.2.c.3 | Branch circuiting |  | 100 | LF | 10 | 1000 | 1000
| 2.3 | Fire Alarm
| 2.3.a |  | 2.3.a.1 | 100' telephone cabling in 1"RGS |  | 100 | LF | 10 | 1000 | 1000 | 61000
|  |  | 2.3.a.2 | N/A
|  |  | 2.3.a.3 | Fire alarm system (including notification devices & fire alarm panel) |  | 6000 | SF | 10 | 60000 | 60000
| 2.3.b |  | 2.3.b.1 | 100' telephone cabling in 1"RGS |  | 100 | LF | 10 | 1000 | 1000 | 61000
|  |  | 2.3.b.2 | N/A
|  |  | 2.3.b.3 | Fire alarm system (including notification devices & fire alarm panel) |  | 6000 | SF | 10 | 60000 | 60000
| 3 | Plumbing
| 3.1 | Domestic Water
| 3.1.a |  | 3.1.a.1 | Visual water meter inspection or BMS |  | 1 | Ea | 2500 | 2500 | 23500 | 59500
|  |  |  | Domestic water piping to unit - 3" Copper |  | 300 | LF | 70 | 21000
|  |  | 3.1.a.2 | N/A
|  |  | 3.1.a.3 | Water distribution Cold - 3" Copper |  | 300 | LF | 120 | 36000 | 36000
| 3.2 | Hot Water
| 3.2.a |  | 3.2.a.1 | 750CFH to load additionally to building HW system | [5 empty] | 21700 | 57700
|  |  |  | Domestic water piping to unit - 3" Copper |  | 300 | LF | 70 | 21000
|  |  |  | Sub - meter |  | 1 | Ea | 700 | 700
|  |  | 3.2.a.2 | N/A
|  |  | 3.2.a.3 | Water distribution Hot - 3" Copper |  | 300 | LF | 120 | 36000 | 36000
| 3.2.b |  | 3.2.b.1 | 750CFH to load additionally to building HW system | [5 empty] | 700 | 41700
|  |  |  | Sub - meter |  | 1 | Ea | 700 | 700
|  |  | 3.2.b.2 | Storage tank (200 gallons) |  | 1 | Ea | 5000 | 5000 | 5000
|  |  | 3.2.b.3 | Water distribution Hot - 3" Copper |  | 300 | LF | 120 | 36000 | 36000
| 3.2.c |  | 3.2.c.1 | N/A | [6 empty] | 2000
|  |  | 3.2.c.2 | N/A
|  |  | 3.2.c.3 | Instant water heaters |  | 1 | EA | 2000 | 2000 | 2000
| 3.3 | Sanitary Waste and Vent
| 3.3.a |  | 3.3.a.1 | Dropped floor slab (kitchen areas) |  |  |  | 0 | 0 | 0 | 0
|  |  |  | Pit |  |  |  | 0 | 0
|  |  |  | Framing |  |  |  | 0 | 0
|  |  | 3.3.a.2 | N/A
|  |  | 3.3.a.3 | Floating level floor
| 3.3.b |  | 3.3.b.1 | 4" PVC capped waste pipe |  | 300 | LF | 10 | 3000 | 4040 | 5080
|  |  |  | 2" cap vent |  | 8 | Ea | 130 | 1040
|  |  | 3.3.b.2 | N/A
|  |  | 3.3.b.3 | 2" cap vent |  | 8 | Ea | 130 | 1040 | 1040
| 3.3.c |  | 3.3.c.1 | Trench |  |  | 0 | 0 | 0 | 4040 | 5080
|  |  |  | 4" PVC capped waste pipe |  | 300 | LF | 10 | 3000
|  |  |  | 2" cap vent |  | 8 | Ea | 130 | 1040
|  |  | 3.3.c.2 | N/A
|  |  | 3.3.c.3 | 2" cap vent |  | 8 | Ea | 130 | 1040 | 1040
| 3.4 | Grease Waste
| 3.4.a |  | 3.4.a.1 | N/A | [6 empty] | 0
|  |  | 3.4.a.2 | N/A
|  |  | 3.4.a.3 | N/A
| 3.4.b |  | 3.4.b.1 | N/A | [6 empty] | 0
|  |  | 3.4.b.2 | N/A
|  |  | 3.4.b.3 | N/A
| 3.5 | Gas
| 3.5.a |  | 3.5.a.1 | N/A | [6 empty] | 0
|  |  | 3.5.a.2 | N/A
|  |  | 3.5.a.3 | N/A
| 3.5.b |  | 3.5.b.1 | N/A | [6 empty] | 0
|  |  | 3.5.b.2 | N/A
|  |  | 3.5.b.3 | N/A
Fire Protection Systems
| 3.6 | Wet Sprinkler System
| 3.6.a |  | 3.6.a.1 | Sprinklers |  | 6000 | SF | 10 | 60000 | 62600 | 62600
|  |  |  | 3" floor control assembly |  | 1 | Ea | 2600 | 2600
|  |  | 3.6.a.2 | N/A
|  |  | 3.6.a.3 | N/A
| 3.7 | Standpipe System

## HealthCare
Tenant Use Type |  |  |  | Health Care Center
Tenant Area (SF) |  |  |  | 4000
Building Height |  |  |  | 150
# bathrooms |  |  |  | 6
# units |  |  |  | 130
[5 empty] | Notes | Quantity | Unit | Unit Cost | Total Cost | Total cost per Cost Alloc. | Total Cost per Option
| 1 | Mechanical
| 1.1 | Heating
| 1.1.a |  | 1.1.a.1 | 1 - 1/2" pipes at 20deg delta |  | 100 | LF | 60 | 6000 | 52500 | 68500
|  |  |  | Steel pipe 1" - 2" |  | 100 | LF | 70 | 7000
|  |  |  | Incremental Base Building Heat Source Increase by x MBH |  | 160 | MBH | 200 | 32000
|  |  |  | Meters: Flow & Temp |  | 3 | Ea | 2500 | 7500
|  |  | 1.1.a.2 | Electric unit heaters |  | 2 | Ea | 8000 | 16000 | 16000
|  |  | 1.1.a.3 | Included in AHU
| 1.1.b |  | 1.1.b.1 | Included in Cooling System | [6 empty] | 0
|  |  | 1.1.b.2 | N/A
|  |  | 1.1.b.3 | N/A
| 1.1.c |  | 1.1.c.1 | N/A | [6 empty] | 0
|  |  | 1.1.c.2 | N/A
|  |  | 1.1.c.3 | N/A
| 1.1.d |  | 1.1.d.1 | 1 bms point meter |  | 1 | Ea | 2500 | 2500 | 12500 | 44500
|  |  |  | Flue stainless steel exit roof |  | 1 | Ea | 10000 | 10000
|  |  |  | Shaft 18" x 18" (OD) |  |  | LF | 0 | 0
|  |  | 1.1.d.2 | Boiler |  | 160 | MBH | 200 | 32000 | 32000
|  |  | 1.1.d.3 | Boiler |  | 0 | MBH | 200 | 0 | 0
| 1.2 | Cooling
| 1.2.a |  | 1.2.a.1 | 2" pipe at 14deg delta |  | 300 | LF | 80 | 24000 | 94500 | 94500
|  |  |  | Steel pipe 4" - 6" |  | 300 | LF | 210 | 63000
|  |  |  | 3 BMS points Meters: Flow & Temp |  | 3 | Ea | 2500 | 7500
|  |  | 1.2.a.2 | N/A
|  |  | 1.2.a.3 | Included in AHU
| 1.2.b |  | 1.2.b.1 | 2" pipe at 14deg delta |  | 300 | LF | 80 | 24000 | 63000 | 63000
|  |  |  | Steel pipe 3" - 4" |  | 300 | LF | 130 | 39000
|  |  | 1.2.b.2 | N/A
|  |  | 1.2.b.3 | Included in AHU
| 1.2.c |  | 1.2.c.1 | Shaft for refrig. Pipe |  | 150 | LF | 0 | 0 | 0 | 67500
|  |  | 1.2.c.2 | Roof Top Condenser Unit |  | 1 | Ea | 30000 | 30000 | 67500
|  |  |  | Refrigerant piping: 6" diameter Black Steel |  | 150 | LF | 210 | 31500
|  |  |  | 1" copper pipe |  | 150 | LF | 40 | 6000
|  |  | 1.2.c.3 | Included in AHU |  |  |  | 0 | 0 | 0
| 1.2.d |  | 1.2.d.1 | Shaft for refrig. Pipe |  | 150 | LF | 0 | 0 | 0 | 67500
|  |  | 1.2.d.2 | Roof Top Condenser Unit |  | 1 | Ea | 30000 | 30000 | 67500
|  |  |  | Refrigerant piping: 6" diameter Black Steel |  | 150 | LF | 210 | 31500
|  |  |  | 1" copper pipe |  | 150 | LF | 40 | 6000
|  |  | 1.2.d.3 | Included in AHU
| 1.2.e |  | 1.2.e.1 | N/A | [6 empty] | 0
| 1.3 | Ventilation
| 1.3.a |  | 1.3.a.1 | 1.84 SF Louver | Assumet qty | 3 | Ea | 500 | 1500 | 1500 | 61500
|  |  | 1.3.a.2 | Ducting from Louver to AHU |  | 300 | LF | 200 | 60000 | 60000
|  |  | 1.3.a.3 | AHU (Filters, mixing sections, heating coil, cooling coil, fan, return fan, duct work, grills) | Included in AHU line item |  |  | 0 | 0 | 0
| 1.4 | Air-Side Economizers
| 1.4.a |  | 1.4.a.1 | Included in AHU | [6 empty] | 0
|  |  | 1.4.1.2 | Included in AHU
|  |  | 1.4.a.3 | Included in AHU
| 1.5 | Exhaust Air
| 1.5.a |  | 1.5.a.1 | Toilet exhaust fan | Assumed qty | 1 | Ea | 5000 | 5000 | 6000 | 17000
|  |  |  | Louver - Toilet |  | 1 | Ea | 1000 | 1000
|  |  |  | Tenant & public restrooms |  |  |  | 0 | 0
|  |  | 1.5.a.2 | Duct from Louver to fan |  | 30 | LF | 200 | 6000 | 11000
|  |  |  | Toilet exhaust fan |  | 1 | Ea | 5000 | 5000
1.5.a.3
| 1.6 | Kitchen Exhaust
| 1.6.a |  | 1.6.a.1 | N/A | [6 empty] | 0
|  |  | 1.6.a.2 | N/A
|  |  | 1.6.a.3 | N/A
| 1.7 | Air-Handling Units
| 1.7.a |  | 1.7.a.1 | N/A | [6 empty] | 27500
|  |  | 1.7.a.2 | N/A
|  |  | 1.7.a.3 | 1.5CFM / SF | 6000 |  |  |  |  | 27500
|  |  |  | AHU: Inside - Multizone - 6,000 CFM | Assumed this one is selected | 1 | EA | 27500 | 27500
|  |  |  | AHU: Inside - Single - 6,000 CFM |  |  | EA | 22500 | 0
|  |  |  | AHU: Outside - Multizone - 6,000 CFM |  |  | EA | 87880 | 0
|  |  |  | AHU: Outside - Single - 6,000 CFM |  |  | EA | 87880 | 0
| 1.7.b |  | 1.7.b.1 | N/A | [6 empty] | 27500
|  |  | 1.7.b.2 | N/A
|  |  | 1.7.b.3 | 1.5CFM / SF | 6000 |  |  |  |  | 27500
|  |  |  | AHU: Inside - Multizone - 6,000 CFM | Assumed this one is selected | 1 | EA | 27500 | 27500
|  |  |  | AHU: Inside - Single - 6,000 CFM |  |  | EA | 22500 | 0
|  |  |  | AHU: Outside - Multizone - 6,000 CFM |  |  | EA | 87880 | 0
|  |  |  | AHU: Outside - Single - 6,000 CFM |  |  | EA | 87880 | 0
| 1.7.c |  | 1.7.c.1 | N/A | [6 empty] | 27500
|  |  | 1.7.c.2 | N/A
|  |  | 1.7.c.3 | 1.5CFM / SF | 6000 |  |  |  |  | 27500
|  |  |  | AHU: Inside - Multizone - 6,000 CFM | Assumed this one is selected | 1 | EA | 27500 | 27500
|  |  |  | AHU: Inside - Single - 6,000 CFM |  |  | EA | 22500 | 0
|  |  |  | AHU: Outside - Multizone - 6,000 CFM |  |  | EA | 87880 | 0
|  |  |  | AHU: Outside - Single - 6,000 CFM |  |  | EA | 87880 | 0
| 1.7.d |  | 1.7.d.1 | N/A | [6 empty] | 27500
|  |  | 1.7.d.2 | N/A
|  |  | 1.7.d.3 | 1.5CFM / SF | 6000 |  |  |  |  | 27500
|  |  |  | AHU: Inside - Multizone - 6,000 CFM | Assumed this one is selected | 1 | EA | 27500 | 27500
|  |  |  | AHU: Inside - Single - 6,000 CFM |  |  | EA | 22500 | 0
|  |  |  | AHU: Outside - Multizone - 6,000 CFM |  |  | EA | 87880 | 0
|  |  |  | AHU: Outside - Single - 6,000 CFM |  |  | EA | 87880 | 0
| 1.8 | Intakes and Exhaust
| 1.8.a |  | 1.8.a.1 | 1.84 SF Louver | Assumed qty | 3 | Ea | 500 | 1500 | 1500 | 1500
|  |  | 1.8.a.2 | N/A
|  |  | 1.8.a.3 | N/A
| 1.8.b |  | 1.8.b.1 | Goose neck at Roof |  | 1 | Ea | 5000 | 5000 | 65000 | 65000
|  |  |  | Duct through shaft to unit |  | 300 | LF | 200 | 60000
|  |  | 1.8.b.2 | N/A
1.8.b.3
| 2 | Electrical
| 2.1 | Separate metering for electricity by utility
| 2.1.a |  | 2.1.a.1 | 150 amp - 208Y/120V three phase electrical service / cost covered by Con Edison | [5 empty] | 3300 | 4300
|  |  |  | CT Cabinet - 150A |  | 1 | EA | 1550 | 1550
|  |  |  | Service Switch - 150A |  | 1 | EA | 1750 | 1750
|  |  | 2.1.a.2 | N/A
|  |  | 2.1.a.3 | Branch circuiting |  | 100 | LF | 10 | 1000 | 1000
| 2.1.b |  | 2.1.b.1 | 1 sets of (4) 1/0 + (1)#6g in 2"c 100' | Landlord will pay for it | 100 | LF | 40 | 4000 | 6450 | 7450
|  |  |  | Service Switch - 150A |  | 1 | EA | 1750 | 1750
|  |  |  | Sub - meter |  | 1 | EA | 700 | 700
|  |  | 2.1.b.2 | N/A
|  |  | 2.1.b.3 | Branch circuiting |  | 100 | LF | 10 | 1000 | 1000
| 2.2 | Emergency Power
| 2.2.a |  | 2.2.a.1 | N/A | [6 empty] | 450
|  |  | 2.2.a.2 | N/A
|  |  | 2.2.a.3 | Emergency light fixtures (90 min battery pack) | Assumed qty | 3 | Ea | 150 | 450 | 450
| 2.2.b |  | 2.2.b.1 | N/A | [6 empty] | 9650
|  |  | 2.2.b.2 | N/A
|  |  | 2.2.b.3 | New gas service | [5 empty] | 9650
|  |  |  | 3.5 KW natural gas generator + 15A 3 pole disconnect switch |  | 1 | Ea | 9650 | 9650
| 2.2.c |  | 2.2.c.1 | [6 empty] | 12650 | 13650
|  |  |  | (4)#10 + (1)#2g in 1"c 100' |  | 100 | LF | 30 | 3000
|  |  |  | 3.5 KW natural gas generator + 15A 3 pole disconnect switch |  | 1 | Ea | 9650 | 9650
|  |  | 2.2.c.2 | N/A
|  |  | 2.2.c.3 | Branch circuiting |  | 100 | LF | 10 | 1000 | 1000
| 2.3 | Fire Alarm
| 2.3.a |  | 2.3.a.1 | 100' telephone cabling in 1"RGS |  | 100 | LF | 10 | 1000 | 1000 | 42240
|  |  | 2.3.a.2 | N/A
|  |  | 2.3.a.3 | Fire alarm system (including notification devices & fire alarm panel) |  | 4000 | SF | 10 | 40000 | 41240
|  |  |  | Notification devices |  | 2 | Ea | 220 | 440
|  |  |  | Fire alarm panel |  | 1 | Ea | 800 | 800
| 2.3.b |  | 2.3.b.1 | 100' telephone cabling in 1"RGS |  | 100 | LF | 4.91 | 491 | 491 | 40491
|  |  | 2.3.b.2 | N/A
|  |  | 2.3.b.3 | Fire alarm system (including notification devices & fire alarm panel) |  | 4000 | SF | 10 | 40000 | 40000
| 3 | Plumbing
| 3.1 | Domestic Water
| 3.1.a |  | 3.1.a.1 | Visual water meter inspection or BMS |  | 1 | EA | 2500 | 2500 | 23500 | 59500
|  |  |  | Domestic water piping to unit - 3" Copper |  | 300 | LF | 70 | 21000
|  |  | 3.1.a.2 | N/A
|  |  | 3.1.a.3 | Water distribution Cold - 3" Copper |  | 300 | LF | 120 | 36000 | 36000
| 3.2 | Hot Water
| 3.2.a |  | 3.2.a.1 | 750CFH to load additionally to building HW system |  |  |  | 0 | 0 | 21700 | 57700
|  |  |  | Domestic water piping to unit - 3" Copper |  | 300 | LF | 70 | 21000
|  |  |  | Sub - meter |  | 1 | EA | 700 | 700
|  |  | 3.2.a.2 | N/A
|  |  | 3.2.a.3 | Water distribution Hot - 3" Copper |  | 300 | LF | 120 | 36000 | 36000
| 3.2.b |  | 3.2.b.1 | 750CFH to load additionally to building HW system |  |  |  | 0 | 0 | 700 | 5700
|  |  |  | Sub - meter |  | 1 | EA | 700 | 700
|  |  | 3.2.b.2 | Storage tank (200 gallons) |  | 1 | EA | 5000 | 5000 | 5000
|  |  | 3.2.b.3 | Water distribution Hot - 3" Copper |  |  |  | 120 | 0 | 0
| 3.2.c |  | 3.2.c.1 | N/A | [6 empty] | 2000
|  |  | 3.2.c.2 | N/A
|  |  | 3.2.c.3 | Instant water heaters | Assumed qty | 1 | EA | 2000 | 2000 | 2000
| 3.3 | Sanitary Waste and Vent
| 3.3.a |  | 3.3.a.1 | Dropped floor slab (kitchen areas) |  |  |  | 0 | 0 | 0 | 0
|  |  |  | Pit |  |  |  | 0 | 0
|  |  |  | Framing |  |  |  | 0 | 0
|  |  | 3.3.a.2 | N/A
|  |  | 3.3.a.3 | Floating level floor |  |  |  | 0 | 0 | 0
| 3.3.b |  | 3.3.b.1 | 4" PVC capped waste pipe |  | 300 | LF | 10 | 3000 | 4040 | 5080
|  |  |  | 2" cap vent |  | 8 | Ea | 130 | 1040
|  |  | 3.3.b.2 | N/A
|  |  | 3.3.b.3 | 2" cap vent |  | 8 | Ea | 130 | 1040 | 1040
| 3.3.c |  | 3.3.c.1 | Trench |  |  |  | 0 | 0 | 4040 | 5080
|  |  |  | 4" PVC capped waste pipe |  | 300 | LF | 10 | 3000
|  |  |  | 2" cap vent |  | 8 | Ea | 130 | 1040
|  |  | 3.3.c.2 | N/A
|  |  | 3.3.c.3 | 2" cap vent |  | 8 | Ea | 130 | 1040 | 1040
| 3.4 | Grease Waste
| 3.4.a |  | 3.4.a.1 | N/A | [6 empty] | 0
|  |  | 3.4.a.2 | N/A
|  |  | 3.4.a.3 | N/A
| 3.4.b |  | 3.4.b.1 | N/A | [6 empty] | 0
|  |  | 3.4.b.2 | N/A
|  |  | 3.4.b.3 | N/A
| 3.5 | Gas
| 3.5.a |  | 3.5.a.1 | N/A | [6 empty] | 0
|  |  | 3.5.a.2 | N/A
|  |  | 3.5.a.3 | N/A
| 3.5.b |  | 3.5.b.1 | N/A | [6 empty] | 0
|  |  | 3.5.b.2 | N/A
|  |  | 3.5.b.3 | N/A
Fire Protection Systems
| 3.6 | Wet Sprinkler System
| 3.6.a |  | 3.6.a.1 | Sprinklers |  | 4000 | SF | 10 | 40000 | 42600 | 42600
|  |  |  | 3" floor control assembly |  | 1 | EA | 2600 | 2600
|  |  | 3.6.a.2 | N/A
|  |  | 3.6.a.3 | N/A
| 3.7 | Standpipe System

## Restaurant
Tenant Use Type |  |  |  | Full service restaurant
Tenant Area (SF) |  |  |  | 4000
Building Height |  |  |  | 150
# bathrooms |  |  |  | 8
# units |  |  |  | 130
[5 empty] | Notes | Quantity | Unit | Unit Cost | Total Cost | Total cost per Cost Alloc. | Total Cost per Option
| 1 | Mechanical
| 1.1 | Heating
| 1.1.a |  | 1.1.a.1 | 2" pipes at 20deg delta |  | 100 | LF | 80 | 8000 | 92500 | 108500
|  |  |  | Steel pipe 2" - 4" |  | 100 | LF | 130 | 13000
|  |  |  | Incremental Base Building Heat Source Increase by x MBH |  | 320 | MBH | 200 | 64000
|  |  |  | Meters: Flow & Temp |  | 3 | Ea | 2500 | 7500
|  |  | 1.1.a.2 | Electric unit heaters |  | 2 | Ea | 8000 | 16000 | 16000
|  |  | 1.1.a.3 | Included in AHU
| 1.1.b |  | 1.1.b.1 | Included in Cooling System | [6 empty] | 0
|  |  | 1.1.b.2 | N/A
|  |  | 1.1.b.3 | N/A
| 1.1.c |  | 1.1.c.1 | N/A | [6 empty] | 0
|  |  | 1.1.c.2 | N/A
|  |  | 1.1.c.3 | N/A
| 1.1.d |  | 1.1.d.1 | 1 bms point meter |  | 1 | Ea | 2500 | 2500 | 12500 | 76500
|  |  |  | Flue stainless steel exit roof |  | 1 | Ea | 10000 | 10000
|  |  |  | Shaft 18" x 18" (OD) |  |  | LF |  | 0
|  |  | 1.1.d.2 | Boiler |  | 320 | MBH | 200 | 64000 | 64000
|  |  | 1.1.d.3 | Boiler |  | 0 | MBH | 200 | 0 | 0
| 1.2 | Cooling
| 1.2.a |  | 1.2.a.1 | 2" pipe at 14deg delta |  | 300 | LF | 80 | 24000 | 94500 | 94500
|  |  |  | Steel pipe 4" - 6" |  | 300 | LF | 210 | 63000
|  |  |  | 3 BMS points Meters: Flow & Temp |  | 3 | Ea | 2500 | 7500
|  |  | 1.2.a.2 | N/A
|  |  | 1.2.a.3 | Included in AHU
| 1.2.b |  | 1.2.b.1 | 2 - 1/2" pipe at 14deg delta |  | 300 | LF | 100 | 30000 | 69000 | 69000
|  |  |  | Steel pipe 3" - 4" |  | 300 | LF | 130 | 39000
|  |  | 1.2.b.2 | N/A
|  |  | 1.2.b.3 | Included in AHU
| 1.2.c |  | 1.2.c.1 | Shaft for refrig. Pipe |  | 150 | LF | 0 | 0 | 0 | 67500
|  |  | 1.2.c.2 | Roof Top Condenser Unit |  | 1 | Ea | 30000 | 30000 | 67500
|  |  |  | Refrigerant piping: 6" diameter Black Steel |  | 150 | LF | 210 | 31500
|  |  |  | 1" copper pipe |  | 150 | LF | 40 | 6000
|  |  | 1.2.c.3 | Included in AHU |  |  |  | 0 | 0 | 0
| 1.2.d |  | 1.2.d.1 | Shaft for refrig. Pipe |  | 150 | LF | 0 | 0 | 0 | 67500
|  |  | 1.2.d.2 | Roof Top Condenser Unit |  | 1 | Ea | 30000 | 30000 | 67500
|  |  |  | Refrigerant piping: 6" diameter Black Steel |  | 150 | LF | 210 | 31500
|  |  |  | 1" copper pipe |  | 150 | LF | 40 | 6000
|  |  | 1.2.d.3 | Included in AHU
| 1.2.e |  | 1.2.e.1 | N/A | [6 empty] | 0
| 1.3 | Ventilation
| 1.3.a |  | 1.3.a.1 | 2.88 SF Louver |  | 3 | Ea | 1000 | 3000 | 63000 | 63000
|  |  | 1.3.a.2 | Ducting from Louver to AHU |  | 300 | LF | 200 | 60000
|  |  | 1.3.a.3 | AHU (Filters, mixing sections, heating coil, cooling coil, fan, return fan, duct work, grills) | Included in AHU line item | 1 | Ea | 0 | 0
| 1.4 | Air-Side Economizers
| 1.4.a |  | 1.4.a.1 | Included in AHU | [6 empty] | 0
|  |  | 1.4.1.2 | Included in AHU
|  |  | 1.4.a.3 | Included in AHU
| 1.5 | Exhaust Air
| 1.5.a |  | 1.5.a.1 | Toilet exhaust fan |  | 2 | Ea | 5000 | 10000 | 12000 | 34000
|  |  |  | Louver - Toilet |  | 2 | Ea | 1000 | 2000
Tenant & public restrooms
|  |  | 1.5.a.2 | Duct from Louver to fan | Assumed 30 LF / bathroom | 60 | LF | 200 | 12000 | 22000
|  |  |  | Toilet exhaust fan |  | 2 | Ea | 5000 | 10000
|  |  | 1.5.a.3 | [6 empty] | 0
| 1.6 | Kitchen Exhaust
| 1.6.a |  | 1.6.a.1 | 9 SF Louver |  | 2 | Ea | 800 | 1600 | 1600 | 26600
|  |  | 1.6.a.2 | Kitchen exhaust fan |  | 1 | Ea | 10000 | 10000 | 10000
|  |  | 1.6.a.3 | Exhaust hood |  | 1 | Ea | 15000 | 15000 | 15000
| 1.7 | Air-Handling Units
| 1.7.a |  | 1.7.a.1 | N/A | [6 empty] | 35000
|  |  | 1.7.a.2 | N/A
|  |  | 1.7.a.3 | 2 CFM / SF | 8000 |  |  |  | 0 | 35000
|  |  |  | AHU: Inside - Multizone - 8,000 CFM | Assumed this one is selected | 1 | Ea | 35000 | 35000
|  |  |  | AHU: Inside - Single - 8,000 CFM |  |  | Ea | 31630 | 0
|  |  |  | AHU: Outside - Multizone - 8,000 CFM |  |  | Ea | 87880 | 0
|  |  |  | AHU: Outside - Single - 8,000 CFM |  |  | Ea | 87880 | 0
| 1.7.b |  | 1.7.b.1 | N/A | [6 empty] | 35000
|  |  | 1.7.b.2 | N/A
|  |  | 1.7.b.3 | 2 CFM / SF | 8000 |  |  |  | 0 | 35000
|  |  |  | AHU: Inside - Multizone - 8,000 CFM | Assumed this one is selected | 1 | Ea | 35000 | 35000
|  |  |  | AHU: Inside - Single - 8,000 CFM |  |  | Ea | 31630 | 0
|  |  |  | AHU: Outside - Multizone - 8,000 CFM |  |  | Ea | 87880 | 0
|  |  |  | AHU: Outside - Single - 8,000 CFM |  |  | Ea | 87880 | 0
| 1.7.c |  | 1.7.c.1 | N/A | [6 empty] | 35000
|  |  | 1.7.c.2 | N/A
|  |  | 1.7.c.3 | 2 CFM / SF | 8000 |  |  |  | 0 | 35000
|  |  |  | AHU: Inside - Multizone - 8,000 CFM | Assumed this one is selected | 1 | Ea | 35000 | 35000
|  |  |  | AHU: Inside - Single - 8,000 CFM |  |  | Ea | 31630 | 0
|  |  |  | AHU: Outside - Multizone - 8,000 CFM |  |  | Ea | 87880 | 0
|  |  |  | AHU: Outside - Single - 8,000 CFM |  |  | Ea | 87880 | 0
| 1.7.d |  | 1.7.d.1 | N/A | [6 empty] | 35000
|  |  | 1.7.d.2 | N/A
|  |  | 1.7.d.3 | 2 CFM / SF | 8000 |  |  |  | 0 | 35000
|  |  |  | AHU: Inside - Multizone - 8,000 CFM | Assumed this one is selected | 1 | Ea | 35000 | 35000
|  |  |  | AHU: Inside - Single - 8,000 CFM |  |  | Ea | 31630 | 0
|  |  |  | AHU: Outside - Multizone - 8,000 CFM |  |  | Ea | 87880 | 0
|  |  |  | AHU: Outside - Single - 8,000 CFM |  |  | Ea | 87880 | 0
| 1.8 | Intakes and Exhaust
| 1.8.a |  | 1.8.a.1 | 2.88 SF Louver |  | 3 | Ea | 1000 | 3000 | 3000 | 3000
|  |  | 1.8.a.2 | N/A
|  |  | 1.8.a.3 | N/A
| 1.8.b |  | 1.8.b.1 | Goose neck at Roof |  | 1 | Ea | 5000 | 5000 | 65000 | 65000
|  |  |  | Duct through shaft to unit |  | 300 | LF | 200 | 60000
|  |  | 1.8.b.2 | N/A
|  |  | 1.8.b.3 | [6 empty] | 0
| 2 | Electrical
| 2.1 | Separate metering for electricity by utility
| 2.1.a |  | 2.1.a.1 | 400 amp - 208Y/120V three phase electrical service / cost covered by Con Edison | [5 empty] | 6850 | 7850
|  |  |  | CT Cabinet - 400A |  | 1 | Ea | 1850 | 1850
|  |  |  | Service Switch - 400A |  | 1 | Ea | 5000 | 5000
|  |  | 2.1.a.2 | N/A
|  |  | 2.1.a.3 | Branch circuiting |  | 100 | LF | 10 | 1000 | 1000
| 2.1.b |  | 2.1.b.1 | 1 sets of (4) 1/0 + (1)#6g in 3 1/2"c 100' | Landlord will pay for it | 100 | LF | 40 | 4000 | 9700 | 10700
|  |  |  | Service Switch - 400A |  | 1 | Ea | 5000 | 5000
|  |  |  | Sub - meter |  | 1 | Ea | 700 | 700
|  |  | 2.1.b.2 | N/A
|  |  | 2.1.b.3 | Branch circuiting |  | 100 | LF | 10 | 1000 | 1000
| 2.2 | Emergency Power
| 2.2.a |  | 2.2.a.1 | N/A | [6 empty] | 450
|  |  | 2.2.a.2 | N/A
|  |  | 2.2.a.3 | Emergency light fixtures (90 min battery pack) |  | 3 | Ea | 150 | 450 | 450
| 2.2.b |  | 2.2.b.1 | N/A | [6 empty] | 21000
|  |  | 2.2.b.2 | N/A
|  |  | 2.2.b.3 | [6 empty] | 21000
|  |  |  | 10 KW natural gas generator + 30A 3pole disconnect switch |  | 1 | Ea | 21000 | 21000
| 2.2.c |  | 2.2.c.1 | [6 empty] | 24000 | 25000
|  |  |  | (4)#10 + (1)#2g in 1"c 100' |  | 100 | LF | 30 | 3000
|  |  |  | 10 KW natural gas generator + 30A 3pole disconnect switch |  | 1 | Ea | 21000 | 21000
|  |  | 2.2.c.2 | N/A
|  |  | 2.2.c.3 | Branch circuiting |  | 100 | LF | 10 | 1000 | 1000
| 2.3 | Fire Alarm
| 2.3.a |  | 2.3.a.1 | 100' telephone cabling in 1"RGS |  | 100 | LF | 10 | 1000 | 1000 | 41000
|  |  | 2.3.a.2 | N/A
|  |  | 2.3.a.3 | Fire alarm system (including notification devices & fire alarm panel) |  | 4000 | SF | 10 | 40000 | 40000
| 2.3.b |  | 2.3.b.1 | 100' telephone cabling in 1"RGS |  | 100 | LF | 10 | 1000 | 1000 | 41000
|  |  | 2.3.b.2 | N/A
|  |  | 2.3.b.3 | Fire alarm system (including notification devices & fire alarm panel) |  | 4000 | SF | 10 | 40000 | 40000
| 3 | Plumbing
| 3.1 | Domestic Water
| 3.1.a |  | 3.1.a.1 | Visual water meter inspection or BMS |  | 1 | Ea | 2500 | 2500 | 23500 | 59500
|  |  |  | Domestic water piping to unit - 3" Copper |  | 300 | LF | 70 | 21000
|  |  | 3.1.a.2 | N/A
|  |  | 3.1.a.3 | Water distribution Cold - 3" Copper |  | 300 | LF | 120 | 36000 | 36000
| 3.2 | Hot Water
| 3.2.a |  | 3.2.a.1 | 750CFH to load additionally to building HW system |  |  |  |  | 0 | 21700 | 57700
|  |  |  | Domestic water piping to unit - 3" Copper |  | 300 | LF | 70 | 21000
|  |  |  | Sub - meter |  | 1 | Ea | 700 | 700
|  |  | 3.2.a.2 | N/A
|  |  | 3.2.a.3 | Water distribution Hot - 3" Copper |  | 300 | LF | 120 | 36000 | 36000
| 3.2.b |  | 3.2.b.1 | [6 empty] | 700 | 41700
|  |  |  | Sub - meter |  | 1 | Ea | 700 | 700
|  |  | 3.2.b.2 | Storage tank (200 gallons) |  | 1 | Ea | 5000 | 5000 | 5000
|  |  | 3.2.b.3 | Water distribution Hot - 3" Copper |  | 300 | LF | 120 | 36000 | 36000
| 3.2.c |  | 3.2.c.1 | N/A | [6 empty] | 2000
|  |  | 3.2.c.2 | N/A
|  |  | 3.2.c.3 | Instant water heaters |  | 1 | EA | 2000 | 2000 | 2000
| 3.3 | Sanitary Waste and Vent
| 3.3.a |  | 3.3.a.1 | Dropped floor slab (kitchen areas) |  |  |  | 0 | 0 | 0 | 0
|  |  |  | Pit |  |  |  | 0 | 0
|  |  |  | Framing |  |  |  | 0 | 0
|  |  | 3.3.a.2 | N/A
|  |  | 3.3.a.3 | Floating level floor |  |  |  | 0 | 0 | 0
| 3.3.b |  | 3.3.b.1 | 4" PVC capped waste pipe |  | 300 | LF | 10 | 3000 | 4040 | 5080
|  |  |  | 2" cap vent |  | 8 | Ea | 130 | 1040
|  |  | 3.3.b.2 | N/A
|  |  | 3.3.b.3 | 2" cap vent |  | 8 | Ea | 130 | 1040 | 1040
| 3.3.c |  | 3.3.c.1 | Trench | [5 empty] | 4040 | 5080
|  |  |  | 4" PVC capped waste pipe |  | 300 | LF | 10 | 3000
|  |  |  | 2" cap vent |  | 8 | Ea | 130 | 1040
|  |  | 3.3.c.2 | N/A
|  |  | 3.3.c.3 | 2" cap vent |  | 8 | Ea | 130 | 1040 | 1040
| 3.4 | Grease Waste
| 3.4.a |  | 3.4.a.1 | N/A | [6 empty] | 2500
|  |  | 3.4.a.2 | Grease interceptor |  | 1 | Ea | 2500 | 2500 | 2500
|  |  | 3.4.a.3 | N/A
| 3.4.b |  | 3.4.b.1 | N/A | [6 empty] | 0
|  |  | 3.4.b.2 | N/A
|  |  | 3.4.b.3 | N/A
| 3.5 | Gas
| 3.5.a |  | 3.5.a.1 | Gas booster |  | 1 | Ea | 5000 | 5000 | 5000 | 16000
|  |  | 3.5.a.2 | N/A
|  |  | 3.5.a.3 | 3" gas pipe | Length? Material? Diam? | 100 | LF | 110 | 11000 | 11000
| 3.5.b |  | 3.5.b.1 | 3" gas pipe | MATERIAL? | 100 | LF | 110 | 11000 | 11000 | 11000
|  |  | 3.5.b.2 | N/A
|  |  | 3.5.b.3 | N/A
Fire Protection Systems
| 3.6 | Wet Sprinkler System
| 3.6.a |  | 3.6.a.1 | Sprinklers |  | 4000 | SF | 10 | 40000 | 42600 | 42600
|  |  |  | 3" floor control assembly |  | 1 | Ea | 2600 | 2600
|  |  | 3.6.a.2 | N/A
|  |  | 3.6.a.3 | N/A
| 3.7 | Standpipe System

## GenRetL
Tenant Use Type |  |  |  | General retail (Large)
Tenant Area (SF) |  |  |  | 4000
Building Height |  |  |  | 150
# bathrooms |  |  |  | 2
# units |  |  |  | 130
[5 empty] | Notes | Quantity | Unit | Unit Cost | Total Cost | Total cost per Cost Alloc. | Total Cost per Option
| 1 | Mechanical
| 1.1 | Heating
| 1.1.a |  | 1.1.a.1 | 1 - 1/2" pipes at 20deg delta |  | 100 | LF | 60 | 6000 | 47500 | 63500
|  |  |  | Steel pipe 1" - 2" |  | 100 | LF | 70 | 7000
|  |  |  | Incremental Base Building Heat Source Increase by x MBH |  | 160 | MBH | 200 | 32000
|  |  |  | Meters: Flow & Temp |  | 1 | Ea | 2500 | 2500
|  |  | 1.1.a.2 | Electric unit heaters |  | 2 | Ea | 8000 | 16000 | 16000
|  |  | 1.1.a.3 | Included in AHU
| 1.1.b |  | 1.1.b.1 | Included in Cooling System | [6 empty] | 0
|  |  | 1.1.b.2 | N/A
|  |  | 1.1.b.3 | N/A
| 1.1.c |  | 1.1.c.1 | N/A | [6 empty] | 0
|  |  | 1.1.c.2 | N/A
|  |  | 1.1.c.3 | N/A
| 1.1.d |  | 1.1.d.1 | 1 bms point meter |  | 1 | Ea | 2500 | 2500 | 12500 | 44500
|  |  |  | Flue stainless steel exit roof |  | 1 | Ea | 10000 | 10000
|  |  |  | Shaft 18" x 18" (OD) |  |  | LF |  | 0
|  |  | 1.1.d.2 | Boiler |  | 160 | MBH | 200 | 32000 | 32000
|  |  | 1.1.d.3 | Boiler |  | 0 | MBH | 200 | 0 | 0
| 1.2 | Cooling
| 1.2.a |  | 1.2.a.1 | 2" pipe at 14deg delta |  | 300 | LF | 80 | 24000 | 94500 | 94500
|  |  |  | Steel pipe 4" - 6" |  | 300 | LF | 210 | 63000
|  |  |  | 3 BMS points Meters: Flow & Temp |  | 3 | Ea | 2500 | 7500
|  |  | 1.2.a.2 | N/A
|  |  | 1.2.a.3 | Included in AHU
| 1.2.b |  | 1.2.b.1 | 2" pipe at 14deg delta |  | 300 | LF | 80 | 24000 | 63000 | 63000
|  |  |  | Steel pipe 3" - 4" |  | 300 | LF | 130 | 39000
|  |  | 1.2.b.2 | N/A
|  |  | 1.2.b.3 | Included in AHU
| 1.2.c |  | 1.2.c.1 | Shaft for refrig. Pipe |  | 150 | LF | 0 | 0 | 0 | 67500
|  |  | 1.2.c.2 | Roof Top Condenser Unit |  | 1 | Ea | 30000 | 30000 | 67500
|  |  |  | Refrigerant piping: 6" diameter Black Steel |  | 150 | LF | 210 | 31500
|  |  |  | 1" copper pipe |  | 150 | LF | 40 | 6000
|  |  | 1.2.c.3 | Included in AHU
| 1.2.d |  | 1.2.d.1 | Shaft for refrig. Pipe |  | 150 | LF | 0 | 0 | 0 | 67500
|  |  | 1.2.d.2 | Roof Top Condenser Unit |  | 1 | Ea | 30000 | 30000 | 67500
|  |  |  | Refrigerant piping: 6" diameter Black Steel |  | 150 | LF | 210 | 31500
|  |  |  | 1" copper pipe |  | 150 | LF | 40 | 6000
|  |  | 1.2.d.3 | Included in AHU
| 1.2.e |  | 1.2.e.1 | N/A | [6 empty] | 0
| 1.3 | Ventilation
| 1.3.a |  | 1.3.a.1 | 1.84 Sf Louver |  | 4 | Ea | 500 | 2000 | 2000 | 62000
|  |  | 1.3.a.2 | Ducting from Louver to AHU |  | 300 | LF | 200 | 60000 | 60000
|  |  | 1.3.a.3 | AHU (Filters, mixing sections, heating coil, cooling coil, fan, return fan, duct work, grills) | Included in AHU line item |  | Ea | 0 | 0 | 0
| 1.4 | Air-Side Economizers
| 1.4.a |  | 1.4.a.1 | Included in AHU | [6 empty] | 0
|  |  | 1.4.1.2 | Included in AHU
|  |  | 1.4.a.3 | Included in AHU
| 1.5 | Exhaust Air
| 1.5.a |  | 1.5.a.1 | Toilet exhaust fan |  | 1 | Ea | 5000 | 5000 | 6000 | 17000
|  |  |  | Louver - Toilet |  | 1 | Ea | 1000 | 1000
|  |  |  | Tenant & public restrooms |  |  |  |  | 0
|  |  | 1.5.a.2 | Duct from Louver to fan |  | 30 | LF | 200 | 6000 | 11000
|  |  |  | Toilet exhaust fan |  | 1 | Ea | 5000 | 5000
|  |  | 1.5.a.3 | N/A | [5 empty] | 0
| 1.6 | Kitchen Exhaust
| 1.6.a |  | 1.6.a.1 | N/A | [6 empty] | 0
|  |  | 1.6.a.2 | N/A
|  |  | 1.6.a.3 | N/A
| 1.7 | Air-Handling Units
| 1.7.a |  | 1.7.a.1 | N/A | [6 empty] | 27500
|  |  | 1.7.a.2 | N/A
|  |  | 1.7.a.3 | 1.6 CFM / SF | 6400 |  |  |  |  | 27500
|  |  |  | AHU: Inside - Multizone - 6,400 CFM | Assumed this one is selected | 1 | Ea | 27500 | 27500
|  |  |  | AHU: Inside - Single - 6,400 CFM |  |  | Ea | 22500 | 0
|  |  |  | AHU: Outside - Multizone - 6,400 CFM |  |  | Ea | 87880 | 0
|  |  |  | AHU: Outside - Single - 6,400 CFM |  |  | Ea | 87880 | 0
| 1.7.b |  | 1.7.b.1 | N/A | [6 empty] | 27500
|  |  | 1.7.b.2 | N/A
|  |  | 1.7.b.3 | 1.6 CFM / SF | 6400 |  |  |  | 0 | 27500
|  |  |  | AHU: Inside - Multizone - 6,400 CFM | Assumed this one is selected | 1 | Ea | 27500 | 27500
|  |  |  | AHU: Inside - Single - 6,400 CFM |  |  | Ea | 22500 | 0
|  |  |  | AHU: Outside - Multizone - 6,400 CFM |  |  | Ea | 87880 | 0
|  |  |  | AHU: Outside - Single - 6,400 CFM |  |  | Ea | 87880 | 0
| 1.7.c |  | 1.7.c.1 | N/A | [6 empty] | 27500
|  |  | 1.7.c.2 | N/A
|  |  | 1.7.c.3 | 1.6 CFM / SF | 6400 |  |  |  | 0 | 27500
|  |  |  | AHU: Inside - Multizone - 6,400 CFM | Assumed this one is selected | 1 | Ea | 27500 | 27500
|  |  |  | AHU: Inside - Single - 6,400 CFM |  |  | Ea | 22500 | 0
|  |  |  | AHU: Outside - Multizone - 6,400 CFM |  |  | Ea | 87880 | 0
|  |  |  | AHU: Outside - Single - 6,400 CFM |  |  | Ea | 87880 | 0
| 1.7.d |  | 1.7.d.1 | N/A | [6 empty] | 27500
|  |  | 1.7.d.2 | N/A
|  |  | 1.7.d.3 | 1.6 CFM / SF | 6400 |  |  |  | 0 | 27500
|  |  |  | AHU: Inside - Multizone - 6,400 CFM | Assumed this one is selected | 1 | Ea | 27500 | 27500
|  |  |  | AHU: Inside - Single - 6,400 CFM |  |  | Ea | 22500 | 0
|  |  |  | AHU: Outside - Multizone - 6,400 CFM |  |  | Ea | 87880 | 0
|  |  |  | AHU: Outside - Single - 6,400 CFM |  |  | Ea | 87880 | 0
| 1.8 | Intakes and Exhaust
| 1.8.a |  | 1.8.a.1 | 1.84 SF Louver |  | 4 | Ea | 500 | 2000 | 2000 | 2000
|  |  | 1.8.a.2 | N/A
|  |  | 1.8.a.3 | N/A
| 1.8.b |  | 1.8.b.1 | Goose neck at Roof |  | 1 | Ea | 5000 | 5000 | 65000 | 65000
|  |  |  | Duct through shaft to unit |  | 300 | LF | 200 | 60000
|  |  | 1.8.b.2 | N/A
|  |  | 1.8.b.3 | N/A
| 2 | Electrical
| 2.1 | Separate metering for electricity by utility
| 2.1.a |  | 2.1.a.1 | 200 amp - 208Y/120V three phase electrical service / cost covered by Con Edison |  |  |  | 0 | 0 | 3300 | 4300
|  |  |  | CT Cabinet - 200A |  | 1 | Ea | 1550 | 1550
|  |  |  | Service Switch - 200A |  | 1 | Ea | 1750 | 1750
|  |  | 2.1.a.2 | N/A
|  |  | 2.1.a.3 | Branch circuiting |  | 100 | LF | 10 | 1000 | 1000
| 2.1.b |  | 2.1.b.1 | 1 sets of (4) 3/0 + (1)#2g in 2 1/2"c 100' | Landlord will pay for it | 100 | LF | 50 | 5000 | 7450 | 8450
|  |  |  | Service Switch - 200A |  | 1 | Ea | 1750 | 1750
|  |  |  | Sub - meter |  | 1 | Ea | 700 | 700
|  |  | 2.1.b.2 | N/A
|  |  | 2.1.b.3 | Branch circuiting |  | 100 | LF | 10 | 1000 | 1000
| 2.2 | Emergency Power
| 2.2.a |  | 2.2.a.1 | N/A | [6 empty] | 600
|  |  | 2.2.a.2 | N/A
|  |  | 2.2.a.3 | Emergency light fixtures (90 min battery pack) |  | 4 | Ea | 150 | 600 | 600
| 2.2.b |  | 2.2.b.1 | N/A | [6 empty] | 10340
|  |  | 2.2.b.2 | N/A
|  |  | 2.2.b.3 | New gas service |  |  |  | 0 | 0 | 10340
|  |  |  | 5 KW gas generator with 15A 3pole disconnect switch |  | 1 | Ea | 10340 | 10340
| 2.2.c |  | 2.2.c.1 | [6 empty] | 13340 | 14340
|  |  |  | (4)#10 + (1)#2g in 1"c 100' |  | 100 | LF | 30 | 3000
|  |  |  | 5 KW gas generator with 15A 3pole disconnect switch |  | 1 | Ea | 10340 | 10340
|  |  | 2.2.c.2 | N/A
|  |  | 2.2.c.3 | Branch circuiting |  | 100 | LF | 10 | 1000 | 1000
| 2.3 | Fire Alarm
| 2.3.a |  | 2.3.a.1 | 100' telephone cabling in 1"RGS |  | 100 | LF | 10 | 1000 | 1000 | 41000
|  |  | 2.3.a.2 | N/A
|  |  | 2.3.a.3 | Fire alarm system (including notification devices & fire alarm panel) |  | 4000 | SF | 10 | 40000 | 40000
| 2.3.b |  | 2.3.b.1 | 100' telephone cabling in 1"RGS |  | 100 | LF | 10 | 1000 | 1000 | 41000
|  |  | 2.3.b.2 | N/A
|  |  | 2.3.b.3 | Fire alarm system (including notification devices & fire alarm panel) |  | 4000 | SF | 10 | 40000 | 40000
| 3 | Plumbing
| 3.1 | Domestic Water
| 3.1.a |  | 3.1.a.1 | Visual water meter inspection or BMS |  | 1 | Ea | 2500 | 2500 | 23500 | 59500
|  |  |  | Domestic water piping to unit - 3" Copper |  | 300 | LF | 70 | 21000
|  |  | 3.1.a.2 | N/A
|  |  | 3.1.a.3 | Water distribution Cold - 3" Copper |  | 300 | LF | 120 | 36000 | 36000
| 3.2 | Hot Water
| 3.2.a |  | 3.2.a.1 | N/A | [5 empty] | 0 | 0
N/A
N/A
|  |  | 3.2.a.2 | N/A
|  |  | 3.2.a.3 | N/A | [5 empty] | 0
| 3.2.b |  | 3.2.b.1 | N/A | [5 empty] | 0 | 0
N/A
|  |  | 3.2.b.2 | N/A | [5 empty] | 0
|  |  | 3.2.b.3 | N/A | [5 empty] | 0
| 3.2.c |  | 3.2.c.1 | N/A | [6 empty] | 2000
|  |  | 3.2.c.2 | N/A
|  |  | 3.2.c.3 | Instant water heaters |  | 1 | EA | 2000 | 2000 | 2000
| 3.3 | Sanitary Waste and Vent
| 3.3.a |  | 3.3.a.1 | Dropped floor slab (kitchen areas) |  |  |  | 0 | 0 | 0 | 0
|  |  |  | Pit |  |  |  | 0 | 0
|  |  |  | Framing |  |  |  | 0 | 0
|  |  | 3.3.a.2 | N/A
|  |  | 3.3.a.3 | Floating level floor |  |  |  | 0 | 0 | 0
| 3.3.b |  | 3.3.b.1 | 4" PVC capped waste pipe |  | 300 | LF | 10 | 3000 | 4040 | 5080
|  |  |  | 2" cap vent |  | 8 | Ea | 130 | 1040
|  |  | 3.3.b.2 | N/A
|  |  | 3.3.b.3 | 2" cap vent |  | 8 | Ea | 130 | 1040 | 1040
| 3.3.c |  | 3.3.c.1 | Trench |  |  | 0 | 0 | 0 | 4040 | 5080
|  |  |  | 4" PVC capped waste pipe |  | 300 | LF | 10 | 3000
|  |  |  | 2" cap vent |  | 8 | Ea | 130 | 1040
|  |  | 3.3.c.2 | N/A
|  |  | 3.3.c.3 | 2" cap vent |  | 8 | Ea | 130 | 1040 | 1040
| 3.4 | Grease Waste
| 3.4.a |  | 3.4.a.1 | N/A | [6 empty] | 0
|  |  | 3.4.a.2 | N/A
|  |  | 3.4.a.3 | N/A
| 3.4.b |  | 3.4.b.1 | N/A | [6 empty] | 0
|  |  | 3.4.b.2 | N/A
|  |  | 3.4.b.3 | N/A
| 3.5 | Gas
| 3.5.a |  | 3.5.a.1 | N/A | [6 empty] | 0
|  |  | 3.5.a.2 | N/A
|  |  | 3.5.a.3 | N/A
| 3.5.b |  | 3.5.b.1 | N/A | [6 empty] | 0
|  |  | 3.5.b.2 | N/A
|  |  | 3.5.b.3 | N/A
Fire Protection Systems
| 3.6 | Wet Sprinkler System
| 3.6.a |  | 3.6.a.1 | Sprinklers |  | 4000 | SF | 10 | 40000 | 42600 | 42600
|  |  |  | 3" floor control assembly |  | 1 | Ea | 2600 | 2600
|  |  | 3.6.a.2 | N/A
|  |  | 3.6.a.3 | N/A
| 3.7 | Standpipe System

## GenRetS
Tenant Use Type |  |  |  | General retail (Small)
Tenant Area (SF) |  |  |  | 2000
Building Height |  |  |  | 150
# bathrooms |  |  |  | 1
# units |  |  |  | 130
[5 empty] | Notes | Quantity | Unit | Unit Cost | Total Cost | Total cost per Cost Alloc. | Total Cost per Option
| 1 | Mechanical
| 1.1 | Heating
| 1.1.a |  | 1.1.a.1 | 1" pipes at 20deg delta |  | 100 | LF | 40 | 4000 | 29500 | 37500
|  |  |  | Steel pipe 1" - 2" |  | 100 | LF | 70 | 7000
|  |  |  | Incremental Base Building Heat Source Increase by x MBH |  | 80 | MBH | 200 | 16000
|  |  |  | Meters: Flow & Temp |  | 1 | Ea | 2500 | 2500
|  |  | 1.1.a.2 | Electric Unit Heaters |  | 1 | Ea | 8000 | 8000 | 8000
|  |  | 1.1.a.3 | Included in AHU
| 1.1.b |  | 1.1.b.1 | Included in Cooling System | [6 empty] | 0
|  |  | 1.1.b.2 | N/A
|  |  | 1.1.b.3 | N/A
| 1.1.c |  | 1.1.c.1 | N/A | [6 empty] | 0
|  |  | 1.1.c.2 | N/A
|  |  | 1.1.c.3 | N/A
| 1.1.d |  | 1.1.d.1 | 1 bms point meter |  | 1 | Ea | 2500 | 2500 | 12500 | 28500
|  |  |  | Flue stainless steel exit roof |  | 1 | Ea | 10000 | 10000
|  |  |  | Shaft 18" x 18" (OD) |  |  | LF |  | 0
|  |  | 1.1.d.2 | Boiler |  | 80 | MBH | 200 | 16000 | 16000
|  |  | 1.1.d.3 | Boiler |  | 0 | MBH | 200 | 0 | 0
| 1.2 | Cooling
| 1.2.a |  | 1.2.a.1 | 1 - 1/4" pipe at 14deg delta |  | 300 | LF | 50 | 15000 | 85500 | 85500
|  |  |  | Steel pipe 4" - 6" |  | 300 | LF | 210 | 63000
|  |  |  | 3 BMS points Meters: Flow & Temp |  | 3 | Ea | 2500 | 7500
|  |  | 1.2.a.2 | N/A
|  |  | 1.2.a.3 | Included in AHU
| 1.2.b |  | 1.2.b.1 | 1 - 1/4" pipe at 14deg delta |  | 300 | LF | 50 | 15000 | 54000 | 54000
|  |  |  | Steel pipe 3" - 4" |  | 300 | LF | 130 | 39000
|  |  | 1.2.b.2 | N/A
|  |  | 1.2.b.3 | Included in AHU
| 1.2.c |  | 1.2.c.1 | Shaft for refrig. Pipe |  | 150 | LF | 0 |  |  | 67500
|  |  | 1.2.c.2 | Roof Top Condenser Unit |  | 1 | Ea | 30000 | 30000 | 67500
|  |  |  | Refrigerant piping: 6" diameter Black Steel |  | 150 | LF | 210 | 31500
|  |  |  | 1" copper pipe |  | 150 | LF | 40 | 6000
|  |  | 1.2.c.3 | Included in AHU
| 1.2.d |  | 1.2.d.1 | Shaft for refrig. Pipe |  | 150 | LF | 0 |  |  | 67500
|  |  | 1.2.d.2 | Roof Top Condenser Unit |  | 1 | Ea | 30000 | 30000 | 67500
|  |  |  | Refrigerant piping: 6" diameter Black Steel |  | 150 | LF | 210 | 31500
|  |  |  | 1" copper pipe |  | 150 | LF | 40 | 6000
|  |  | 1.2.d.3 | Included in AHU
| 1.2.e |  | 1.2.e.1 | Evaporator and condenser included in AHU LINE ITEM | [6 empty] | 0
| 1.3 | Ventilation
| 1.3.a |  | 1.3.a.1 | 0.93 SF Louver |  | 2 | Ea | 500 | 1000 | 1000 | 61000
|  |  | 1.3.a.2 | Ducting from Louver to AHU |  | 300 | LF | 200 | 60000 | 60000
|  |  | 1.3.a.3 | AHU (Filters, mixing sections, heating coil, cooling coil, fan, return fan, duct work, grills) | Included in AHU line item |  | Ea | 0 | 0 | 0
| 1.4 | Air-Side Economizers
| 1.4.a |  | 1.4.a.1 | Included in AHU | [6 empty] | 0
|  |  | 1.4.1.2 | Included in AHU
|  |  | 1.4.a.3 | Included in AHU
| 1.5 | Exhaust Air
| 1.5.a |  | 1.5.a.1 | Toilet exhaust fan |  | 1 | Ea | 5000 | 5000 | 6000 | 17000
|  |  |  | Louver - Toilet |  | 1 | Ea | 1000 | 1000
Tenant & public restrooms
|  |  | 1.5.a.2 | Duct from Louver to fan |  | 30 | LF | 200 | 6000 | 11000
|  |  |  | Toilet exhaust fan |  | 1 | Ea | 5000 | 5000
|  |  | 1.5.a.3 | N/A
| 1.6 | Kitchen Exhaust
| 1.6.a |  | 1.6.a.1 | N/A | [6 empty] | 0
|  |  | 1.6.a.2 | N/A
|  |  | 1.6.a.3 | N/A
| 1.7 | Air-Handling Units
| 1.7.a |  | 1.7.a.1 | N/A | [6 empty] | 19000
|  |  | 1.7.a.2 | N/A
|  |  | 1.7.a.3 | 1.6 CFM / SF | 3200 |  |  |  |  | 19000
|  |  |  | AHU: Inside - Multizone - 3,200 CFM | Assumed this one is selected | 1 | Ea | 19000 | 19000
|  |  |  | AHU: Inside - Single - 3,200 CFM |  |  | Ea | 15130 | 0
|  |  |  | AHU: Outside - Multizone - 3,200 CFM |  |  | Ea | 44380 | 0
|  |  |  | AHU: Outside - Single - 3,200 CFM |  |  | Ea | 44380 | 0
| 1.7.b |  | 1.7.b.1 | N/A | [6 empty] | 19000
|  |  | 1.7.b.2 | N/A
|  |  | 1.7.b.3 | 1.6 CFM / SF | 3200 |  |  |  |  | 19000
|  |  |  | AHU: Inside - Multizone - 3,200 CFM | Assumed this one is selected | 1 | Ea | 19000 | 19000
|  |  |  | AHU: Inside - Single - 3,200 CFM |  |  | Ea | 15130 | 0
|  |  |  | AHU: Outside - Multizone - 3,200 CFM |  |  | Ea | 44380 | 0
|  |  |  | AHU: Outside - Single - 3,200 CFM |  |  | Ea | 44380 | 0
| 1.7.c |  | 1.7.c.1 | N/A | [6 empty] | 19000
|  |  | 1.7.c.2 | N/A
|  |  | 1.7.c.3 | 1.6 CFM / SF | 3200 |  |  |  |  | 19000
|  |  |  | AHU: Inside - Multizone - 3,200 CFM | Assumed this one is selected | 1 | Ea | 19000 | 19000
|  |  |  | AHU: Inside - Single - 3,200 CFM |  |  | Ea | 15130 | 0
|  |  |  | AHU: Outside - Multizone - 3,200 CFM |  |  | Ea | 44380 | 0
|  |  |  | AHU: Outside - Single - 3,200 CFM |  |  | Ea | 44380 | 0
| 1.7.d |  | 1.7.d.1 | N/A | [6 empty] | 19000
|  |  | 1.7.d.2 | N/A
|  |  | 1.7.d.3 | 1.6 CFM / SF | 3200 |  |  |  |  | 19000
|  |  |  | AHU: Inside - Multizone - 3,200 CFM | Assumed this one is selected | 1 | Ea | 19000 | 19000
|  |  |  | AHU: Inside - Single - 3,200 CFM |  |  | Ea | 15130 | 0
|  |  |  | AHU: Outside - Multizone - 3,200 CFM |  |  | Ea | 44380 | 0
|  |  |  | AHU: Outside - Single - 3,200 CFM |  |  | Ea | 44380 | 0
| 1.8 | Intakes and Exhaust
| 1.8.a |  | 1.8.a.1 | 0.93 SF Louver |  | 2 | Ea | 500 | 1000 | 1000 | 1000
|  |  | 1.8.a.2 | N/A
|  |  | 1.8.a.3 | N/A
| 1.8.b |  | 1.8.b.1 | Goose neck at Roof |  | 1 | Ea | 5000 | 5000 | 65000 | 65000
|  |  |  | Duct through shaft to unit |  | 300 | LF | 200 | 60000
|  |  | 1.8.b.2 | N/A
|  |  | 1.8.b.3 | N/A
| 2 | Electrical
| 2.1 | Separate metering for electricity by utility
| 2.1.a |  | 2.1.a.1 | 100 amp - 208Y/120V three phase electrical service / cost covered by Con Edison | [5 empty] | 2750 | 3750
|  |  |  | CT Cabinet - 100A |  | 1 | Ea | 1250 | 1250
|  |  |  | Service Switch - 100A |  | 1 | Ea | 1500 | 1500
|  |  | 2.1.a.2 | N/A | [5 empty] | 0
|  |  | 2.1.a.3 | Branch circuiting |  | 100 | LF | 10 | 1000 | 1000
| 2.1.b |  | 2.1.b.1 | 1 sets of (4)#1/0 + (1)#6g in 1 1/2"c 100' | Landlord will pay for it | 100 | LF | 40 | 4000 | 6200 | 7200
|  |  |  | Service Switch - 100A |  | 1 | Ea | 1500 | 1500
|  |  |  | Sub - meter |  | 1 | Ea | 700 | 700
|  |  | 2.1.b.2 | N/A
|  |  | 2.1.b.3 | Branch circuiting |  | 100 | LF | 10 | 1000 | 1000
| 2.2 | Emergency Power
| 2.2.a |  | 2.2.a.1 | N/A | [6 empty] | 300
|  |  | 2.2.a.2 | N/A
|  |  | 2.2.a.3 | Emergency light fixtures (90 min battery pack) |  | 2 | Ea | 150 | 300 | 300
| 2.2.b |  | 2.2.b.1 | N/A | [6 empty] | 9000
|  |  | 2.2.b.2 | N/A
|  |  | 2.2.b.3 | New gas service | [5 empty] | 9000
|  |  |  | 2.5 KW natural gas generator + 20A 3 pole disconnect switch |  | 1 | Ea | 9000 | 9000
| 2.2.c |  | 2.2.c.1 | [6 empty] | 12000 | 13000
|  |  |  | (4)#10 + (1)#2g in 1"c 100' |  | 100 | LF | 30 | 3000
|  |  |  | 2.5 KW natural gas generator + 20A 3 pole disconnect switch |  | 1 | Ea | 9000 | 9000
|  |  | 2.2.c.2 | N/A
|  |  | 2.2.c.3 | Branch circuiting |  | 100 | LF | 10 | 1000 | 1000
| 2.3 | Fire Alarm
| 2.3.a |  | 2.3.a.1 | 100' telephone cabling in 1"RGS |  | 100 | LF | 10 | 1000 | 1000 | 21000
|  |  | 2.3.a.2 | N/A
|  |  | 2.3.a.3 | Fire alarm system (including notification devices & fire alarm panel) |  | 2000 | SF | 10 | 20000 | 20000
0
0
| 2.3.b |  | 2.3.b.1 | 100' telephone cabling in 1"RGS |  | 100 | LF | 10 | 1000 | 1000 | 21000
|  |  | 2.3.b.2 | N/A
|  |  | 2.3.b.3 | Fire alarm system (including notification devices & fire alarm panel) |  | 2000 | SF | 10 | 20000 | 20000
| 3 | Plumbing
| 3.1 | Domestic Water
| 3.1.a |  | 3.1.a.1 | Visual water meter inspection or BMS |  | 1 | Ea | 2500 | 2500 | 9500 | 21500
|  |  |  | Domestic water piping to unit - 3" Copper |  | 100 | LF | 70 | 7000
|  |  | 3.1.a.2 | N/A
|  |  | 3.1.a.3 | Water distribution Cold - 3" Copper |  | 100 | LF | 120 | 12000 | 12000
| 3.2 | Hot Water
| 3.2.a |  | 3.2.a.1 | N/A | [6 empty] | 0
|  |  |  | N/A |  |  | LF | 0 | 0
|  |  |  | N/A |  |  | Ea | 0 | 0
|  |  | 3.2.a.2 | N/A
|  |  | 3.2.a.3 | N/A |  |  | LF | 0 | 0
| 3.2.b |  | 3.2.b.1 | N/A | [6 empty] | 0
|  |  |  | N/A |  |  | Ea | 0 | 0
|  |  | 3.2.b.2 | N/A |  |  | Ea | 0 | 0
|  |  | 3.2.b.3 | N/A |  |  | LF | 0 | 0
| 3.2.c |  | 3.2.c.1 | N/A | [6 empty] | 2000
|  |  | 3.2.c.2 | N/A
|  |  | 3.2.c.3 | Instant water heaters |  | 1 | EA | 2000 | 2000 | 2000
| 3.3 | Sanitary Waste and Vent
| 3.3.a |  | 3.3.a.1 | Dropped floor slab (kitchen areas) | [6 empty] | 0
Pit
Framing
|  |  | 3.3.a.2 | N/A
|  |  | 3.3.a.3 | Floating level floor
| 3.3.b |  | 3.3.b.1 | 4" PVC capped waste pipe |  | 100 | LF | 10 | 1000 | 1260 | 1520
|  |  |  | 2" cap vent |  | 2 | Ea | 130 | 260
|  |  | 3.3.b.2 | N/A
|  |  | 3.3.b.3 | 2" cap vent |  | 2 | Ea | 130 | 260 | 260
| 3.3.c |  | 3.3.c.1 | Trench |  |  | 0 | 0 | 0 | 1260 | 1520
|  |  |  | 4" PVC capped waste pipe |  | 100 | LF | 10 | 1000
|  |  |  | 2" cap vent |  | 2 | Ea | 130 | 260
|  |  | 3.3.c.2 | N/A
|  |  | 3.3.c.3 | 2" cap vent |  | 2 | Ea | 130 | 260 | 260
| 3.4 | Grease Waste
| 3.4.a |  | 3.4.a.1 | N/A | [6 empty] | 0
|  |  | 3.4.a.2 | N/A
|  |  | 3.4.a.3 | N/A
| 3.4.b |  | 3.4.b.1 | N/A | [6 empty] | 0
|  |  | 3.4.b.2 | N/A
|  |  | 3.4.b.3 | N/A
| 3.5 | Gas
| 3.5.a |  | 3.5.a.1 | N/A | [6 empty] | 0
|  |  | 3.5.a.2 | N/A
|  |  | 3.5.a.3 | N/A
| 3.5.b |  | 3.5.b.1 | N/A | [6 empty] | 0
|  |  | 3.5.b.2 | N/A
|  |  | 3.5.b.3 | N/A
Fire Protection Systems
| 3.6 | Wet Sprinkler System
| 3.6.a |  | 3.6.a.1 | Sprinklers |  | 2000 | SF | 10 | 20000 | 22600 | 22600
|  |  |  | 3" floor control assembly |  | 1 | Ea | 2600 | 2600
|  |  | 3.6.a.2 | N/A
|  |  | 3.6.a.3 | N/A
| 3.7 | Standpipe System

## Laundr
Tenant Use Type |  |  |  | Laundromat
Tenant Area (SF) |  |  |  | 2000
Building Height |  |  |  | 150
# bathrooms |  |  |  | 0
# units |  |  |  | 130
[5 empty] | Notes | Quantity | Unit | Unit Cost | Total Cost | Total cost per Cost Alloc. | Total Cost per Option
| 1 | Mechanical
| 1.1 | Heating
| 1.1.a |  | 1.1.a.1 | 1 - 1/2" pipes at 20deg delta |  | 100 | LF | 60 | 6000 | 58500 | 66500
|  |  |  | Steel pipe 2" - 4" |  | 100 | LF | 130 | 13000
|  |  |  | Incremental Base Building Heat Source Increase by x MBH |  | 160 | MBH | 200 | 32000
|  |  |  | Meters: Flow & Temp |  | 3 | Ea | 2500 | 7500
|  |  | 1.1.a.2 | Electric unit heaters |  | 1 | Ea | 8000 | 8000 | 8000
|  |  | 1.1.a.3 | Included in AHU
| 1.1.b |  | 1.1.b.1 | Included in Cooling System | [6 empty] | 0
|  |  | 1.1.b.2 | N/A
|  |  | 1.1.b.3 | N/A
| 1.1.c |  | 1.1.c.1 | N/A | [6 empty] | 0
|  |  | 1.1.c.2 | N/A
|  |  | 1.1.c.3 | N/A
| 1.1.d |  | 1.1.d.1 | 1 bms point meter |  | 1 | Ea | 2500 | 2500 | 12500 | 44500
|  |  |  | Flue stainless steel exit roof |  | 1 | Ea | 10000 | 10000
|  |  |  | Shaft 18" x 18" (OD) |  |  | LF |  | 0
|  |  | 1.1.d.2 | Boiler |  | 160 | MBH | 200 | 32000 | 32000
|  |  | 1.1.d.3 | Boiler |  | 0 | MBH | 200 | 0 | 0
| 1.2 | Cooling
| 1.2.a |  | 1.2.a.1 | 1 - 1/4" pipe at 14deg delta |  | 300 | LF | 50 | 15000 | 85500 | 85500
|  |  |  | Steel pipe 4" - 6" |  | 300 | LF | 210 | 63000
|  |  |  | 3 BMS points Meters: Flow & Temp |  | 3 | Ea | 2500 | 7500
|  |  | 1.2.a.2 | N/A
|  |  | 1.2.a.3 | Included in AHU
| 1.2.b |  | 1.2.b.1 | 1 - 1/4" pipe at 14deg delta |  | 300 | LF | 50 | 15000 | 54000 | 54000
|  |  |  | Steel pipe 3" - 4" |  | 300 | LF | 130 | 39000
|  |  | 1.2.b.2 | N/A
|  |  | 1.2.b.3 | Included in AHU
| 1.2.c |  | 1.2.c.1 | Shaft for refrig. Pipe |  | 150 | LF |  | 0 | 0 | 67500
|  |  | 1.2.c.2 | Roof Top Condenser Unit |  | 1 | Ea | 30000 | 30000 | 67500
|  |  |  | Refrigerant piping: 6" diameter Black Steel |  | 150 | LF | 210 | 31500
|  |  |  | 1" copper pipe |  | 150 | LF | 40 | 6000
|  |  | 1.2.c.3 | Included in AHU
| 1.2.d |  | 1.2.d.1 | Shaft for refrig. Pipe |  | 150 | LF |  | 0 | 0 | 67500
|  |  | 1.2.d.2 | Roof Top Condenser Unit |  | 1 | Ea | 30000 | 30000 | 67500
|  |  |  | Refrigerant piping: 6" diameter Black Steel |  | 150 | LF | 210 | 31500
|  |  |  | 1" copper pipe |  | 150 | LF | 40 | 6000
|  |  | 1.2.d.3 | Included in AHU
| 1.2.e |  | 1.2.e.1 | N/A | [6 empty] | 0
| 1.3 | Ventilation
| 1.3.a |  | 1.3.a.1 | 0.93 SF Louver |  | 4 | Ea | 500 | 2000 | 2000 | 62000
|  |  | 1.3.a.2 | Ducting from Louver to AHU |  | 300 | LF | 200 | 60000 | 60000
|  |  | 1.3.a.3 | AHU (Filters, mixing sections, heating coil, cooling coil, fan, return fan, duct work, grills) | Included in AHU line item |  | Ea | 0 | 0 | 0
| 1.4 | Air-Side Economizers
| 1.4.a |  | 1.4.a.1 | Included in AHU | [6 empty] | 0
|  |  | 1.4.1.2 | Included in AHU
|  |  | 1.4.a.3 | Included in AHU
| 1.5 | Exhaust Air
| 1.5.a |  | 1.5.a.1 | Toilet exhaust fan | N/A |  | Ea |  |  |  | 0
|  |  |  | Landlord provide Louver | N/A |  | Ea
|  |  |  | Tenant & public restrooms | N/A
|  |  | 1.5.a.2 | Duct from Louver to fan | N/A |  | LF
|  |  |  | Fan | N/A |  | Ea
|  |  | 1.5.a.3 | N/A | [5 empty] | 0
| 1.6 | Kitchen Exhaust
| 1.6.a |  | 1.6.a.1 | N/A | [6 empty] | 0
|  |  | 1.6.a.2 | N/A
|  |  | 1.6.a.3 | N/A
| 1.7 | Air-Handling Units
| 1.7.a |  | 1.7.a.1 | N/A | [6 empty] | 19000
|  |  | 1.7.a.2 | N/A
|  |  | 1.7.a.3 | 1.6 CFM / SF | 3200 |  |  |  |  | 19000
|  |  |  | AHU: Inside - Multizone - 3,200 CFM | Assumed this one is selected | 1 | Ea | 19000 | 19000
|  |  |  | AHU: Inside - Single - 3,200 CFM |  |  | Ea | 15130 | 0
|  |  |  | AHU: Outside - Multizone - 3,200 CFM |  |  | Ea | 44380 | 0
|  |  |  | AHU: Outside - Single - 3,200 CFM |  |  | Ea | 44380 | 0
| 1.7.b |  | 1.7.b.1 | N/A | [6 empty] | 19000
|  |  | 1.7.b.2 | N/A
|  |  | 1.7.b.3 | 1.6 CFM / SF | [5 empty] | 19000
|  |  |  | AHU: Inside - Multizone - 3,200 CFM | Assumed this one is selected | 1 | Ea | 19000 | 19000
|  |  |  | AHU: Inside - Single - 3,200 CFM |  |  | Ea | 15130 | 0
|  |  |  | AHU: Outside - Multizone - 3,200 CFM |  |  | Ea | 44380 | 0
|  |  |  | AHU: Outside - Single - 3,200 CFM |  |  | Ea | 44380 | 0
| 1.7.c |  | 1.7.c.1 | N/A | [6 empty] | 19000
|  |  | 1.7.c.2 | N/A
|  |  | 1.7.c.3 | 1.6 CFM / SF | [5 empty] | 19000
|  |  |  | AHU: Inside - Multizone - 3,200 CFM | Assumed this one is selected | 1 | Ea | 19000 | 19000
|  |  |  | AHU: Inside - Single - 3,200 CFM |  |  | Ea | 15130 | 0
|  |  |  | AHU: Outside - Multizone - 3,200 CFM |  |  | Ea | 44380 | 0
|  |  |  | AHU: Outside - Single - 3,200 CFM |  |  | Ea | 44380 | 0
| 1.7.d |  | 1.7.d.1 | N/A | [6 empty] | 19000
|  |  | 1.7.d.2 | N/A
|  |  | 1.7.d.3 | 1.6 CFM / SF | [5 empty] | 19000
|  |  |  | AHU: Inside - Multizone - 3,200 CFM | Assumed this one is selected | 1 | Ea | 19000 | 19000
|  |  |  | AHU: Inside - Single - 3,200 CFM |  |  | Ea | 15130 | 0
|  |  |  | AHU: Outside - Multizone - 3,200 CFM |  |  | Ea | 44380 | 0
|  |  |  | AHU: Outside - Single - 3,200 CFM |  |  | Ea | 44380 | 0
| 1.8 | Intakes and Exhaust
| 1.8.a |  | 1.8.a.1 | 0.93 SF Louver |  | 4 | Ea | 500 | 2000 | 2000 | 2000
|  |  | 1.8.a.2 | N/A
|  |  | 1.8.a.3 | N/A
| 1.8.b |  | 1.8.b.1 | N/A | [6 empty] | 0
N/A
|  |  | 1.8.b.2 | N/A
|  |  | 1.8.b.3 | N/A
| 2 | Electrical
| 2.1 | Separate metering for electricity by utility
| 2.1.a |  | 2.1.a.1 | 200 amp - 208Y/120V three phase electrical service / cost covered by Con Edison | [5 empty] | 3300 | 4300
|  |  |  | CT Cabinet - 200A |  | 1 | Ea | 1550 | 1550
|  |  |  | Service Switch - 200A |  | 1 | Ea | 1750 | 1750
|  |  | 2.1.a.2 | N/A
|  |  | 2.1.a.3 | Branch circuiting |  | 100 | LF | 10 | 1000 | 1000
| 2.1.b |  | 2.1.b.1 | 1 sets of (4) 3/0 + (1)#2g in 2 1/2"c 100' | Landlord will pay for it | 100 | LF | 50 | 5000 | 7450 | 8450
|  |  |  | Service Switch - 200A |  | 1 | Ea | 1750 | 1750
|  |  |  | Sub - meter |  | 1 | Ea | 700 | 700
|  |  | 2.1.b.2 | N/A
|  |  | 2.1.b.3 | Branch circuiting |  | 100 | LF | 10 | 1000 | 1000
| 2.2 | Emergency Power
| 2.2.a |  | 2.2.a.1 | N/A | [6 empty] | 300
|  |  | 2.2.a.2 | N/A
|  |  | 2.2.a.3 | Emergency light fixtures (90 min battery pack) |  | 2 | Ea | 150 | 300 | 300
|  |  |  | N/A | [5 empty] | 0
| 2.2.b |  | 2.2.b.1 | N/A | [6 empty] | 10340
|  |  | 2.2.b.2 | N/A
|  |  | 2.2.b.3 | New gas service | [5 empty] | 10340
|  |  |  | 5 KW gas generator with 15A 3pole disconnect switch |  | 1 | Ea | 10340 | 10340
| 2.2.c |  | 2.2.c.1 | [6 empty] | 13340 | 14340
|  |  |  | (4)#10 + (1)#2g in 1"c 100' |  | 100 | LF | 30 | 3000
|  |  |  | 5 KW gas generator with 15A 3pole disconnect switch |  | 1 | Ea | 10340 | 10340
|  |  | 2.2.c.2 | N/A
|  |  | 2.2.c.3 | Branch circuiting |  | 100 | LF | 10 | 1000 | 1000
| 2.3 | Fire Alarm
| 2.3.a |  | 2.3.a.1 | 100' telephone cabling in 1"RGS |  | 100 | LF | 10 | 1000 | 1000 | 21000
|  |  | 2.3.a.2 | N/A
|  |  | 2.3.a.3 | Fire alarm system (including notification devices & fire alarm panel) |  | 2000 | SF | 10 | 20000 | 20000
| 2.3.b |  | 2.3.b.1 | 100' telephone cabling in 1"RGS |  | 100 | LF | 10 | 1000 | 1000 | 21000
|  |  | 2.3.b.2 | N/A
|  |  | 2.3.b.3 | Fire alarm system (including notification devices & fire alarm panel) |  | 2000 | SF | 10 | 20000 | 20000
| 3 | Plumbing
| 3.1 | Domestic Water
| 3.1.a |  | 3.1.a.1 | Visual water meter inspection or BMS |  | 1 | Ea | 2500 | 2500 | 23500 | 59500
|  |  |  | Domestic water piping to unit - 3" Copper |  | 300 | LF | 70 | 21000
|  |  | 3.1.a.2 | N/A |  |  |  |  | 0
|  |  | 3.1.a.3 | Water distribution Cold - 3" Copper |  | 300 | LF | 120 | 36000 | 36000
| 3.2 | Hot Water
| 3.2.a |  | 3.2.a.1 | 750CFH to load additionally to building HW system | [5 empty] | 21700 | 57700
|  |  |  | Domestic water piping to unit - 3" Copper |  | 300 | LF | 70 | 21000
|  |  |  | Sub - meter |  | 1 | Ea | 700 | 700
|  |  | 3.2.a.2 | N/A
|  |  | 3.2.a.3 | Water distribution Hot - 3" Copper |  | 300 | LF | 120 | 36000 | 36000
| 3.2.b |  | 3.2.b.1 | 750CFH to load additionally to building HW system | [5 empty] | 700 | 41700
|  |  |  | Sub - meter |  | 1 | Ea | 700 | 700
|  |  | 3.2.b.2 | Storage tank (200 gallons) |  | 1 | Ea | 5000 | 5000 | 5000
|  |  | 3.2.b.3 | Water distribution Hot - 3" Copper |  | 300 | LF | 120 | 36000 | 36000
| 3.2.c |  | 3.2.c.1 | N/A | [6 empty] | 4000
|  |  | 3.2.c.2 | N/A
|  |  | 3.2.c.3 | Instant water heaters |  | 2 | EA | 2000 | 4000 | 4000
| 3.3 | Sanitary Waste and Vent
| 3.3.a |  | 3.3.a.1 | Dropped floor slab (kitchen areas) | [6 empty] | 0
Pit
Framing
|  |  | 3.3.a.2 | N/A
|  |  | 3.3.a.3 | Floating level floor
| 3.3.b |  | 3.3.b.1 | 4" PVC capped waste pipe |  | 300 | LF | 10 | 3000 | 4040 | 5080
|  |  |  | 2" cap vent |  | 8 | Ea | 130 | 1040
|  |  | 3.3.b.2 | N/A
|  |  | 3.3.b.3 | 2" cap vent |  | 8 | Ea | 130 | 1040 | 1040
| 3.3.c |  | 3.3.c.1 | Trench |  |  |  |  | 0 | 4040 | 5080
|  |  |  | 4" PVC capped waste pipe |  | 300 | LF | 10 | 3000
|  |  |  | 2" cap vent |  | 8 | Ea | 130 | 1040
|  |  | 3.3.c.2 | N/A
|  |  | 3.3.c.3 | 2" cap vent |  | 8 | Ea | 130 | 1040 | 1040
| 3.4 | Grease Waste
| 3.4.a |  | 3.4.a.1 | N/A | [6 empty] | 0
|  |  | 3.4.a.2 | N/A
|  |  | 3.4.a.3 | N/A
| 3.4.b |  | 3.4.b.1 | N/A | [6 empty] | 50000
|  |  | 3.4.b.2 | N/A
|  |  | 3.4.b.3 | Interceptor - wire basket |  | 50 | Ea | 1000 | 50000 | 50000
| 3.5 | Gas
| 3.5.a |  | 3.5.a.1 | Gas booster |  | 1 | Ea | 5000 | 5000 | 5000 | 16000
|  |  | 3.5.a.2 | N/A
|  |  | 3.5.a.3 | 3" gas pipe |  | 100 | LF | 110 | 11000 | 11000
| 3.5.b |  | 3.5.b.1 | 3" gas pipe |  | 100 | LF | 110 | 11000 | 11000 | 11000
|  |  | 3.5.b.2 | N/A
|  |  | 3.5.b.3 | N/A
Fire Protection Systems
| 3.6 | Wet Sprinkler System
| 3.6.a |  | 3.6.a.1 | Sprinklers |  | 2000 | SF | 10 | 20000 | 22600 | 22600
|  |  |  | 3" floor control assembly |  | 1 | Ea | 2600 | 2600
|  |  | 3.6.a.2 | N/A
|  |  | 3.6.a.3 | N/A
| 3.7 | Standpipe System

## Line items
Item | Unit | Unit Cost
2" pipes at 20deg delta | LF | 80 | 79.5 | Assumes Type L Copper Pipe + 50% cost inc for valves and fittings
1 - 1/2" pipes at 20deg delta | LF | 60 | 55.5 | Assumes Type L Copper Pipe + 50% cost inc for valves and fittings
1" pipes at 20deg delta | LF | 40 | 39 | Assumes Type L Copper Pipe + 50% cost inc for valves and fittings
Steel pipe 2" - 4" | LF | 130 | 123 | Assumes Sch. 40 4" diam + 50% cost inc for valves and fittings
Steel pipe 1" - 2" | LF | 70 | 66 | Assumes Sch. 40 2" diam + 50% cost inc for valves and fittings
Meters: Flow & Temp | Ea | 2500 | 2500 | Depends on system and manufacturer
Electric Unit Heaters | Ea | 8000 | 8000 | 115 V 2 psi steam; 620 MBH Rsmeans: 238239164366
2" steam pipe | LF | 130 | 127.5 | Assumed Stainless Steel 2" diam Sch. 40 + 50% cost inc for valves and fittings
2" condensate returns | Ea | 7500 | 7500 | http://www.grainger.com/product/4RD30?gclid=CKLl3tW5zMYCFUFufgodUNUDiA&cm_mmc=PPC:GOOGLEPLAA-_-Pumps-_-Condensate%20Pumps-_-4RD30&ef_id=VYIOSgAABd7hq7dA:20150708211303:s
Steam trap | Ea | 1000 | 1000 | Cast Iron body steam trap, 1 1/4". Rsmenas
2 BMS points Meter Condensate Volume | LS | 2500 | 2500 | Depends on system and manufacturer
Steam fired Unit Heaters | Ea | 8000 | 8000 | Depends on system and manufacturer
1" gas pipe | LF | 50 | 42 | RS Means Welded 1" black sch 40 steel
1 BMS point meter | Ea | 2500 | 2500
Flue stainless steel exit roof | Ea | 10000 | 10000 | Assumes specialty fabricated flue and installation
Boiler | MBH | 200 | 200
Incremental Base Building Heat Source Increase by x MBH | MBH | 200 | 200
2 - 1/2" pipe at 14deg delta | LF | 100 | 99 | Assumes Type L Copper Pipe + 50% cost inc for valves and fittings
3" pipe at 14deg delta | LF | 120 | 117 | Assumes Type L Copper Pipe + 50% cost inc for valves and fittings
2" pipe at 14deg delta | LF | 80 | 79.5 | Assumes Type L Copper Pipe + 50% cost inc for valves and fittings
1 - 1/4" pipe at 14deg delta | LF | 50 | 48 | Assumes Type L Copper Pipe + 50% cost inc for valves and fittings
Steel pipe 4" - 6" | LF | 210 | 207 | Assumes Sch. 40 6" diam + 50% cost inc for valves and fittings
3 BMS points Meters: Flow & Temp | Ea | 2500 | 2500
3" copper pipe | LF | 120 | 117 | Assumes Type L Copper Pipe + 50% cost inc for valves and fittings
Steel pipe 3" - 4" | LF | 130 | 123 | Assumes Sch. 40 4" diam + 50% cost inc for valves and fittings
Roof Top Condenser Unit | Ea | 30000 | 30000 | Confirm tons and capacity: and refrigant
Refrigerant piping: 6" diameter Black Steel | LF | 210 | 207 | Assumes Sch. 40 6" diam + 50% cost inc for valves and fittings
1" copper pipe | LF | 40 | 39 | Assumes Type L Copper Pipe + 50% cost inc for valves and fittings
2.88 SF Louver | Ea | 1000 | 1000 | Assumes approx 3sf duct louver at surface
Ducting from Louver to AHU | LF | 200 | 199.5 | Assume $15/lb, duct is 1' x 1.5', @ 2.66lbs/sf
Toilet exhaust fan | Ea | 5000 | 5000 | Check quantity: cost here is per fan installed
Louver - Toilet | Ea | 1000 | 1000 | Assumes approx 3sf duct louver at surface
Duct from Louver to fan | LF | 200 | 199.5 | Assume $15/lb, duct is 1' x 1.5', @ 2.66lbs/sf
Louver - Kitchen | Ea | 1500 | 1500 | Assumes approx 3sf duct louver at surface
Kitchen exhaust fan | Ea | 10000 | 10000 | Assumption: depends on design
Exhaust hood | Ea | 15000 | 15000 | Assumption: depends on design
AHU: Inside - Multizone - 15,600 CFM | Ea | 57500 | 57500 | Add 25% for grills, connections, pad, installation misc.
AHU: Inside - Single - 15,600 CFM | Ea | 53750 | 53750 | Add 25% for grills, connections, pad, installation misc.
AHU: Outside - Multizone - 15,600 CFM | Ea | 127500 | 127500 | Add 25% for grills, connections, pad, installation misc.
AHU: Outside - Single - 15,600 CFM | Ea | 127500 | 127500 | Add 25% for grills, connections, pad, installation misc.
5.52 SF Louver | Ea | 1500 | 1500
AHU: Inside - Multizone - 24,000 CFM | Ea | 90190 | 90187.5 | Add 25% for grills, connections, pad, installation misc.
AHU: Inside - Single - 24,000 CFM | Ea | 73750 | 73750 | Add 25% for grills, connections, pad, installation misc.
AHU: Outside - Multizone - 24,000 CFM | Ea | 221250 | 221250 | Add 25% for grills, connections, pad, installation misc.
AHU: Outside - Single - 24,000 CFM | Ea | 221250 | 221250 | Add 25% for grills, connections, pad, installation misc.
AHU: Inside - Multizone - 12,000 CFM | Ea | 46250 | 46250 | Add 25% for grills, connections, pad, installation misc.
AHU: Inside - Single - 12,000 CFM | Ea | 40000 | 40000 | Add 25% for grills, connections, pad, installation misc.
AHU: Outside - Multizone - 12,000 CFM | Ea | 127500 | 127500 | Add 25% for grills, connections, pad, installation misc.
AHU: Outside - Single - 12,000 CFM | Ea | 127500 | 127500 | Add 25% for grills, connections, pad, installation misc.
1.84 SF Louver | Ea | 500 | 500
AHU: Inside - Multizone - 6,000 CFM | Ea | 27500 | 27500 | Add 25% for grills, connections, pad, installation misc.
AHU: Inside - Single - 6,000 CFM | Ea | 22500 | 22500 | Add 25% for grills, connections, pad, installation misc.
AHU: Outside - Multizone - 6,000 CFM | Ea | 87880 | 87875 | Add 25% for grills, connections, pad, installation misc.
AHU: Outside - Single - 6,000 CFM | Ea | 87880 | 87875 | Add 25% for grills, connections, pad, installation misc.
AHU: Inside - Multizone - 8,000 CFM | Ea | 35000 | 35000 | Add 25% for grills, connections, pad, installation misc.
AHU: Inside - Single - 8,000 CFM | Ea | 31630 | 31625 | Add 25% for grills, connections, pad, installation misc.
AHU: Outside - Multizone - 8,000 CFM | Ea | 87880 | 87875 | Add 25% for grills, connections, pad, installation misc.
AHU: Outside - Single - 8,000 CFM | Ea | 87880 | 87875 | Add 25% for grills, connections, pad, installation misc.
AHU: Inside - Multizone - 6,400 CFM | Ea | 27500 | 27500 | Add 25% for grills, connections, pad, installation misc.
AHU: Inside - Single - 6,400 CFM | Ea | 22500 | 22500 | Add 25% for grills, connections, pad, installation misc.
AHU: Outside - Multizone - 6,400 CFM | Ea | 87880 | 87875 | Add 25% for grills, connections, pad, installation misc.
AHU: Outside - Single - 6,400 CFM | Ea | 87880 | 87875 | Add 25% for grills, connections, pad, installation misc.
0.93 SF Louver | Ea | 500 | 500
AHU: Inside - Multizone - 3,200 CFM | Ea | 19000 | 19000 | Add 25% for grills, connections, pad, installation misc.
AHU: Inside - Single - 3,200 CFM | Ea | 15130 | 15125 | Add 25% for grills, connections, pad, installation misc.
AHU: Outside - Multizone - 3,200 CFM | Ea | 44380 | 44375 | Add 25% for grills, connections, pad, installation misc.
AHU: Outside - Single - 3,200 CFM | Ea | 44380 | 44375 | Add 25% for grills, connections, pad, installation misc.
Goose neck at Roof | Ea | 5000 | 5000 | Non-stainless steel
Duct through shaft to unit | LF | 200 | 199.5 | Assume $15/lb, duct is 1' x 1.5', @ 2.66lbs/sf
CT Cabinet - 800A | Ea | 2550 | 2550
Service Switch - 800A | Ea | 7000 | 7000
CT Cabinet - 400A | Ea | 1850 | 1850
Service Switch - 400A | Ea | 5000 | 5000
Sub - meter | Ea | 700 | 700
Branch Circuiting | LF | 10 | 2 |  | 260519900140 | Wire, copper, stranded | RS MEANS
Emergency light fixtures (90 min battery pack) | Ea | 150 | 150
CT Cabinet - 200A | Ea | 1550 | 1550
Service Switch - 200A | Ea | 1750 | 1750
CT Cabinet - 150A | Ea | 1550 | 1550
Service Switch - 150A | Ea | 1750 | 1750
CT Cabinet - 100A | Ea | 1250 | 1250
Service Switch - 100A | Ea | 1500 | 1500
15 KW natural gas generator + 60A 3pole disconnect switch | Ea | 26000 | 26000
(4)#4 + (1)#8g in 1 1/4"c 100' | LF | 20 | 18.5
100' telephone cabling in 1"RGS | LF | 10 | 4.91
Fire alarm system (including notification devices & fire alarm panel) | SF | 10 | 3
Visual water meter inspection or BMS | Ea | 2500 | 2500
Domestic water piping to unit - 3" Copper | LF | 70 | 61
Water distribution Cold - 3" Copper | LF | 120 | 117 | Assumes Type L Copper Pipe + 50% cost inc for valves and fittings
Storage tank (200 gallons) | Ea | 5000 | 5000
Instant water heaters | Ea | 2000 | 2000
4" PVC capped waste pipe | LF | 10 | 5.45
2" Cap Vent | Ea | 130 | 125
Grease interceptor | Ea | 2500 | 2500
Gas booster | Ea | 5000 | 5000
3" gas pipe | LF | 110 | 100.5 | Assumed 3" Black Steel Sch. 40 + 50% cost inc for valves and fittings
Sprinklers | SF | 10 | 4
2 sets of (4) 500mcm + (1)#1/0g in 3 1/2" c100' | LF | 160 | 155
Water distribution Hot - 3" Copper | LF | 120 | 117 | Assumes Type L Copper Pipe + 50% cost inc for valves and fittings
3" floor control assembly | Ea | 2600 | 2600
4" Copper pipe | LF | 190 | 184.5 | Assumes Type L Copper Pipe + 50% cost inc for valves and fittings
1 set of 4 500mcm + (1)#1/0g in 3 1/2" c100' | LF | 90 | 90
10 KW natural gas generator + 30A 3pole disconnect switch | Ea | 21000 | 21000
(4)#10 + (1)#12g in 1"c 100' | LF | 20 | 13
1 sets of (4) 3/0 + (1)#2g in 2 1/2"c 100' | LF | 50 | 43
5 KW gas generator with 15A 3pole disconnect switch | Ea | 10340 | 10340
(4)#10 + (1)#2g in 1"c 100' | LF | 30 | 22.75
1 sets of (4) 1/0 + (1)#6g in 2"c 100' | LF | 40 | 33.5
3.5 KW natural gas generator + 15A 3 pole disconnect switch | Ea | 9650 | 9650
9 SF Louver | Ea | 800 | 800
1 sets of (4) 1/0 + (1)#6g in 3 1/2"c 100' | LF | 40 | 33.5
1 sets of (4)#1/0 + (1)#6g in 1 1/2"c 100' | LF | 40 | 33.5
2.5 KW natural gas generator + 20A 3 pole disconnect switch | Ea | 9000 | 9000
Interceptor - wire basket | Ea | 1000 | 1000

## Electrical
Kitchen | 32VA/sq.ft
Laundary Mat | 32va/sq.ft
Retail | 15va/sq.ft
Supermarket | 15va/sq.ft
Pharmacy | 8va/sw.ft
Health Care | 10va/sq.ft

## Plumbing
Building Estimate | 15 story
| 110000 | SF
| 130 | units |  | Zone 1 |  |  | Zone 2
| 20000 | SF | Retail |  | 2 bedroom |  |  | 2 bedroom
[5 empty] | 65 |  |  | 65
Gas load for each unit |  | 60 | cfh |  | 120 |  |  | 120
Total cooking load |  | 7800 | cfh |  | 7800 |  |  | 7800
|  |  |  | 7800 |  |  | 7800
Total bathrooms | 130 | 3.6 | WSFU | Demand | Storage |  | Demand | Storage
Total kitchens | 130 | 2.8 | WSFU | 0.14286 | 0.2 |  | 0.14286 | 0.2
|  | 6.4 | WSFU | 1114.2857 | 1560 |  | 1114.2857 | 1560
|  | 832 | WSFU | 2674.2857 |  | gallons | 2674.2857 |  | gallons
|  | 182 | GPM
Required Pipe Size |  | 4"
|  |  |  | Water Heater (WH) # | Heater Location | Zone | GPH | WH (gallons) | QTY | Total WH (gallons) | Required Recovery | BTU Required for 100 Deg Rise | BTU per WH | Actual BTU per WH | Total BTU Required
Laundry Mat
Assume | 75 | CFH PER DRYER |  | 1 | Basement | Low | 2674.2857 | 300 | 2 | 600 | 2074.2857 | 1727880 | 863940 | 1000000 | 2000000
| 3750 | CFH |  | 2 | Basement | Mid | 2674.2857 | 300 | 2 | 600 | 2074.2857 | 1727880 | 863940 | 1000000 | 2000000
[15 empty] | 4000000 | BTU
[14 empty] | WH | 4000 | CFH
[14 empty] | Cooking | 7800
[14 empty] | Total Base Building | 11800 | CFH
[14 empty] | Space Heating | 1445308
1457108
[8 empty] | TW | C2 | C3
[8 empty] | 50 | 28 | 23
[8 empty] | RD | 1680 | 1380
[8 empty] | SR | 672 | 552
[8 empty] | BTU Required for 100 Deg Rise | 1399440 | 1149540
1399.44
[9 empty] | RD | 900
[9 empty] | BTU Required for 100 Deg Rise | 749700
749.7

## Sheet2
Option | Tenant Type | Cost Allocation
a | Supermarket | Developer
b | Pharmacy (L) | Developer + Either party
c
d | Health Care Center | Tenant
e | Full Service Restaurant | Tenant + Either Party
General Retail (L)
General Retail (S)
Laundromat